City of Lebanon

Request for Proposal

RFP # 20-BACKWASH ACTUATORS 11/03
*City of Lebanon reserves the right to reject all or any part of any RFP*

The City of Lebanon is exempt from State Tax and Federal Exercise Tax.

NO PROPOSALS RECEIVED AFTER CLOSING WILL BE ACCEPTED.

The City of Lebanon invites sealed proposals for backwash actuators, in accordance with the specifications and bidding instructions set forth in this Request for Proposals. Bids will be received by the Purchasing Department, 200 N. Castle Heights Avenue, Lebanon, Tennessee 37087, until 10:30 a.m. local time, November 3, 2020, at which time they will be opened and read aloud.

Please identify as a sealed proposal with stamped on the outside of the envelope “RFP #20-BACKWASH ACTUATORS 11/03”

Any questions in regard to this proposal should be directed to Lisa Lane, Purchasing Agent, (615) 443-2802.

A copy of the bid tabulation will be available upon written request to the Purchasing Department.

Any manufacturers’ names, trade names, brand names, or catalog numbers used in the specifications are for the purpose of describing and establishing general quality levels.  Such references are not intended to be restrictive.  Since the “City” does not wish to rule out other competition and equal brands or makes, please remember “ANY APPROVED EQUAL”.  HOWEVER, IF A PRODUCT OTHER THAN SPECIFIED IS BID, IT IS THE VENDORS RESPONSIBILITY TO PROVE TO THE “CITY” THAT SAID PRODUCT IS EQUAL TO OR EXCEEDS THE QUALITY OF THE SPECIFICATIONS LISTED FOR ANY ITEM.

The City of Lebanon is an equal opportunity entity and does not discriminate on the basis of age, race, sex, national origin, religion or disability in admission to, access to, or operations of its programs, services, activities, or in its awarding of such bids.

1. SCOPE AND CLASSIFICATION

1.1 Scope:  The intent of this Request for Proposals and resulting contract is to provide the City of Lebanon with information concerning backwash actuators.
1.2 Classification:  The backwash actuators specifications shall be of the following types either “equal to “or “better than”.

2. SPECIFICATIONS

Backwash Actuators
City of Lebanon Tennessee Water Treatment Plant

 Location:  7 Gilmore Hill Road, Lebanon, TN  37087 

SCOPE

This bid is for (4) four electric actuators for the Water Treatment Plant West Filters 1-4 backwash valves.
New electric actuators will be mounted to existing 12” Pratt 150b butterfly valves. 

Actuator shall meet attached specifications from Beck actuators.

Contractor shall be responsible for removal of existing hydraulic actuator parts, providing new actuators, provide all necessary mounting hardware, wiring, etc.

Note:  existing actuators are hydraulic in nature and as such, new electric, and conduit will have to be provided for new actuators.  

Must provide new switches and valve position indicators to each filter console.

Cleanup and disposal of all existing hardware.

Ensure proper operation in hand, local, and remote settings.

Contractor will work with plant operations staff to minimize downtime during installation.
Contractor must pull all necessary, if any, electrical permits.

Part 1-GENERAL

1.01 THE REQUIREMENT

A. Valve actuators shall be provided with corrosion protection packages to include stainless steel rods, linkages, and hardware.  
B. Valve operators and electric valve actuators shall be designed to unseat, open or close, and seat the valve under the most adverse operating condition to which the valves will be subjected.

C. There shall be no mounting restrictions on the electric valve actuator.

D. The valve operators and electric actuators shall be the full and undivided responsibility of the valve manufacturer in order to ensure complete coordination of the components and to provide unit responsibility.

1.02   WARRANTY AND GUARANTEE
           A.   Warranty and Guarantee shall be as specified in Section 11000


       with the exception that the warranty period shall be for two (2) 

                  years.

PART 2-PRODUCTS

2.01
GENERAL

A. Quarter turn valves 8” and greater in size shall have geared operators.  Gate valves 14” and greater in size shall have geared operators.

B. Operators/actuators shall be furnished with conservatively sized extension bonnets, extension stems, or torque tubes, and all required appurtenances required for a complete installation.  Operators furnished with extension bonnets shall include stainless steel extension stems, or stainless-steel torque tubes.
2.02
MANUAL OPERATORS

A.   Manual operator type shall be as follows:

1. Buried valves shall be equipped with nut operators, extended stems, and valve boxes.  Where the depth of the operating nut is more than 4 feet below finish grade, a valve operator extension shall be provided to bring the operating nut to within 18-24 inches of the surface.

2. Exposed valves up to 6-inch shall be lever operated (except gate valves).

3. Exposed valves 8-inches and larger shall be handwheel operated.

4. Exposed gate valves shall be handwheel operated.

5. Valves with centerline of operator located more than 6-feet above the floor or platform from which it is to be operated shall have a chainwheel operator.

B.   Manual operators shall be rigidly attached to the valve body.

C. All operators shall turn counterclockwise to open and shall have the open direction clearly and permanently marked.

D. Valve operators shall be designed so that the force required to operate the handwheel, lever, or chain (including breakaway torque requirements) does not exceed 80 pounds applied at the extremity of handwheel or chainwheel operator.

E. Handwheels for valves operators shall not be less than 12 inches in diameter.  The maximum diameter of any handwheel shall not exceed 24”.
F. Nut operators shall have standard 2-inch square AWWA operating nuts designed in accordance with AWWA C504-94.

G. Geared manual operators shall be of the worm gear, traveling nut or scotch yolk type except manual operators for butterfly valves 18-inche in diameter or larger which shall be worm gear, unless otherwise indicated in the individual valve specification.  Gear operators shall be of the worm gear or bevel gear type.  Gear box designs incorporating end of travel stops in the housing shall be equipped with AWWA input stops.  Each gearbox shall require a minimum of 10 turns for 90-degree rotation or full valve stem travel and shall be equipped with a mechanical valve position indicator.

H. Manual operators on below grade (and vault installed) valves shall be permanently lubricated and watertight under an external water pressure of 10 psi.

2.03   ELECTRIC VALVE ACTUATORS

A. Position control in modulating valve applications, quarter-turn actuators and two-position in open/close valve applications actuators shall be Group 11 rotary valve drives as manufactured by Harold Beck and Sons, Inc.  Operators shall be furnished with 120-volt, single phase, 60 Hz AC, TENV, permanent magnet, synchronous, inductor motors with NEMA Class F insulation minimum (Class H for modulating actuators), and specifically designed for modulating service or open/close service as specified.  Motor shall be non-coasting, suitable for high duty cycle conditions, and shall be self-locking and self-releasing without the use of a separate brake winding, mechanical brake, or worm gear mechanism.  The motor shall be capable of up to 60 starts/stops per minute or a temporary stall condition without overheating.  Torque capacity of the operators shall be sufficient to operate the valves of at least 1.5.  Maximum current draw of motors shall be 3.1 amperes in a fully stalled condition.  Motors shall reach synchronous speed on start-up in 1.5 AC power cycles and shall also reach dead stop from full synchronous speed in 1.5 cycles.  Motor shall not overheat or fail when in cumulative stall condition for 72 hours.  No electrical or thermal overload protection shall be required for protection of a stalled or cycling operator.

B.   Contractor shall be responsible for selecting valves that do not exceed the maximum torque capacity of the Group 11 actuators manufactured by Harold Beck and Sons.

C. Control drive shall be designed to stay in place upon loss of power and shall be capable of holding a load equal to at least 200% of the model’s rated output.  Stall torque shall be self-limiting not exceeding 2.5 times the rated torque.  Torque switches shall not be required.  Drive shall operate on an increasing signal for full 100” rotation.  Control drives shall be able to operate in any mounting orientation.

D. Gear train shall have high efficiency spur gears constructed of heat-treated alloy steel or ductile iron only.  Readily available gear modules shall provide for a range of torque and timing combinations within the drive’s rated capacity and shall be field-interchangeable.  Gears shall be rated at twice the output torque of the operator, so that a cumulative stall condition of 72 hours will not create any significant wear or performance degradation.  To protect against accumulative stall damage in Auto mode, the drives for modulating actuators should automatically discontinue motor operation when the motor current is detected to be flowing in the same direction for 300 seconds.  Over-travel of operator shall be prevented by internal mechanical stoops cast into the operator.  Operating time between full limits of travel shall be not greater than 180 seconds.

E. Motor pinion and all gearing shall be lubricated with a premium, heavy-duty lithium-based lubricant, and shall not require changing of the lubrication for a minimum of five years.  No oil baths shall be used for lubrication purposes.  Maintenance-free bearings shall be used.

F. A low-speed, disc-type motor, solid handwheel shall be provided, directly connected to the motor’s rotor, for manual operation.  A mechanical indicator of valve position shall be provided and attached to the main output shaft driving the load.  No declutching mechanism shall be required for manual operation.

G. Linkage between operator and valve shall be by crank arms and connecting rod, with adjustable starting point of valve position and adjustable rod length.  Operators shall stop precisely within 0.15 degrees of the desired control position.  Operator output shaft shall be stainless-steel.  Stem shall be self-locking when the motor is de-energized.  Modular construction and special lubrication shall permit the operator to be mounted in any position.  Modulating operators shall be capable of operating in ambient temperatures ranging from -40°F to 185°F.  Direct shaft-to-shaft connection is acceptable only for ball valves less than or equal to 3 inches in diameter.

H. Operators shall be provided with four main individual cast aluminum compartments the motor/gear train compartment, wiring terminal block compartment, and two electronics signal control compartments.  Compartments shall be gasketed and sealed and provided with moisture and dust-proof rigid cast covers.  All switches, wiring, relays, etc., shall be brought to the wiring terminal block compartment for field connection.  Two 1” NPT conduit entries shall be provided with the actuator, one for signal wiring and one for power wiring.  Conduit shall be run properly to avoid water ingress to the compartments.  The motor shall have electrical connections soldered directly to the wiring terminal block where appropriate.  Double lipped grease seals shall be provided on the handwheel and output shafts for weatherproof protection.

I. Two SPDT limit switches for valve full open and full closed position or end-of-travel limit set at the open or close travel range and four auxiliary SPDT limit switches shall be provided on all operators.  Auxiliary limit switches shall be cam-operated, filed adjustable, and with contact rated for 6 amperes at 120 VAC.  Auxiliary limit switches shall be infinitely adjustable over the full range of valve travel.  Limit switches shall be wired to the wiring terminal block compartment for connection to remote device for monitoring purposes.  Drive shall also have integral mechanical stops, capable of preventing over travel of the drive and load, with or without the drive motor.

J. The operators for the modulating valves shall be provided with 4-20 mA output signals for valve position feedback.  Continuous position sensing of valve position shall be provided.  Position sensing device (sensor) shall require no contacting or wiping surface. The position sensing unit shall be provided integral with the operator and shall provide a linear 4-20 mA output signal, proportional to valve percent open.

K. Modulating valve actuators shall be designed to respond to a 4-20mADS analog signal as specified herein

a. Modulating valve actuators designed to respond to a 4-20 MA DC signal shall be provided with a valve positioner which shall position the valve proportional to an externally generated 4-20mADC signal.  The valve positioning control circuitry shall position the valve, in steps down to 0.15”, by comparing the command signal with the present valve position as indicated by the feedback rotary variable differential transformer (RVDT) mechanism.  The control circuitry shall be field adjustable to fail to the “open,” “closed,” or “last” position on loss of 4-20 mA DC command signal.

L. Remote Manual Control Station

1. When a valve assembly and its electric actuator is located at an inaccessible location, remote manual actuator controls shall be furnished in a separate NEMA 4X stainless-steel enclosure (NEMA 7 if located in a hazardous Area Classification as shown on the drawings).  Remote manual control stations shall include a two-position Hand-Auto selector switch, a three-position Open-Off-Close selector switch, a red lamp to indicate valve open, and a green lamp to indicate valve closed.

a.   When the Hand-Auto is in the “Hand” position, open/close control shall be by the open and close selector switch on the remote manual control station.  The “Off” position on the switch shall stop actuator travel.  Unless specified elsewhere, the switch for an open/close service actuator shall be maintained in the open or close position until selected otherwise.  Likewise, the pushbutton or switch for a modulating service actuator shall be spring loaded so as not to maintain that output when an open or close selection is made.

b. When the Hand-Auto is in the “Auto” position, the actuator shall be controlled by remote inputs to the valve actuator from the PLC.

c. Selector switches shall be 30.5 mm, heavy-duty, oil tight NEMA 4X corrosion resistant with legend plates.

d. The remote manual control station shall provide a set of dry contacts to remotely indicate the position of the Hand-Auto switch.  When the Hand-Auto switch is in the “Auto” position, the contacts shall close.  When interconnected to the actuator, this contact shall be wired in series with the auto contact of the actuator’s hand switch, such that taking either switch out of Auto, causes an “Auto” status alarm.

M. Contractor shall coordinate control and wiring with PLC manufacturer and Owner.

N. Certified electrical control schematic diagrams shall be provided by the actuator Manufacturer for each service type of electric actuator.  Interconnecting wiring information shall be submitted including terminal numbers, color coding, and the name and terminal numbers, for items to which the wiring is to be connected.

O. Actuator enclosure shall be aluminum cast, weatherproof, dust-tight, NEMA 4X and IP66/IP68 rated.  Separate conduit entrances shall be available for power and control wiring connections.

P. Local Controls

1.   All electric actuators shall be provided with an integral five-position, drive-mounted electric hand switch to permit local control adjustment or operation on loss of control signal.  The sequence of the hand switch shall be: “AUTO”, “STOP”, “CW”, “STOP”, “CCW”.

a. When the hand switch is in the “Auto” position, the actuator shall be controlled by remote signals from the PLC or from the remote manual control station.

b. When the hand switch is in the “CW” or “CCW” position, the actuator shall move toward the appropriate end-of-travel limit switch.  Placing the selector switch in the “Stop” position shall stop the actuator travel.

c. The hand switch shall provide a set of dry contacts to remotely indicate the position of the Hand-Auto switch on the remote manual control station.  When in Auto, the contacts shall close.

PART 3-EXECUTION

3.01   MANUFACTURER’S FIELD SERVICES


A.   The services of a qualified manufacturer’s technical representative shall be provided.  Equipment General Provisions and shall include the following site visits for electric actuators:

	Service
	Number of Trips
	Number of Days/Trip

	Installation and Testing
	1
	1

	Startup & Training
	1
	1

	Services after Startup
	1
	1


3.02
INSTALLATION

A.   All valve actuators shall be installed in accordance with the manufacturer’s published recommendations and the application specification sections for valves, and motor controls.

B.   Valve actuators shall be factory coated in accordance with the manufacturer’s standard paint system.

3.03
SHOP TESTING


A.   Shop testing certificate shall be provided.

1.   Conduct a complete functional check of each unit.  Correct any deficiencies found in shop testing prior to shipment.

2.   Submit written certification that:

a.   Shop tests for the electrical system and all controls were successfully conducted;

b.   Electrical system and all controls provide the functions specified and required for proper operation of the valve operator system.

3.   Each actuator shall be performance tested and individual test certificates shall be supplied free of charge.  The test equipment shall simulate each typical valve load and the following parameters should be recorded:


a.   Current at maximum torque setting


b.   Torque at maximum torque setting


c.   Flash Test Voltage


d.   Actuator Output Speed or Operating Time


e.   In addition, the test certificate should record details of specification, such as gear ratios for both manual and automatic drive, closing direction, and wiring diagram code number.


f.   Verification of actuator torque rating with valve.

3.04   
FIELD TESTS
A.   Field testing shall be provided with the following additional requirements:

1. Valve actuators shall be field-tested together with the associated valves.

2. Test all valves at the operating pressures at which the particular line will be used.

3. Test all valves for control operation as directed.

4. Field testing shall include optimization of opening and closing times of the valves.  Valve opening and closing times shall be adjusted based on process requirements to optimize operation of the valves.  Final valve opening and closing times as determined by field tests shall be approved by the Engineer prior to final acceptance of the system.

B. Preliminary Field Tests

1.   General:  Preliminary field tests shall be conducted prior to start-up and shall include a functional check of the entire valve operator system and all system components.

2. Scope:   Preliminary field tests shall demonstrate that the valve operator system performs according to specifications and that all equipment, valves, controls, alarms, interlocks, etc., function properly.

3. Based on results of preliminary field tests, the Contractor shall make any adjustments required to settings, etc., to achieve the required valve closing time and operation, as specified or otherwise directed.

C.   Final Field Tests

a. Final Field tests shall be conducted in accordance with the latest revision of AWWA C500.

b. Final field tests shall be conducted simultaneously with the start-up and field testing of the pumps.

c. Final field tests shall be conducted for the full range of operating modes and conditions specified and as directed by the Engineer.  Each of the valves shall be tested at minimum, maximum, and normal head/flow conditions, and under all specified conditions of opening and closing.

Bidders must schedule and on-site visit with either J.C. York or Greg Anderson to verify installation location and answer any questions concerning the scope of work prior to the bid opening date and time.  Contact Phone Number (615) 444-0485.

Bid must include all labor, parts, shipping, training, etc. in the bid price.  

The awarded vendor must schedule installation of the actuators with J.C. York and/or Greg Anderson.

Please state your warranty period and a description of what is covered in the warranty.  (Attach separate sheet describing warranty).

1. INSTRUCTIONS AND CONDITIONS

Deadline and Late Responses.
No bids received after bid opening date and time will be accepted.  Bids postmarked on the bid opening date but received at the Purchasing office after the specified time will be considered late and will be returned unopened.  The City shall not be responsible for bids that are mailed or sent via private delivery services.  The City will not accept bids submitted by fax or electronic mail.

Organization of Bid and Completeness.
Please submit one original bid to the Purchasing office at the address set forth above.  All bids must be sealed and the envelope clearly marked with the bidder’s name and the words, “Backwash Actuators” on other side of sealed envelope; Bid Opening Date: 11/03/2020.  Failure to provide this information on the envelope may result in the bid not being considered.  Bidders must allow sufficient time to ensure receipt of the bid.  It shall be the sole responsibility of the bidder to have the bid delivered to the City before the bid deadline.  

Any negative responses to these questions or failure to respond to these questions will permit the City to refuse to consider the bid.  

Partial or incomplete bids will be rejected.  All bid responses should be typewritten.  If not typewritten, they must be written in ink and clearly legible, and numbers must be expressed in both words and figures.  Erasures, white-outs, typeover’s, and other modifications should be initialed.  Bidders are cautioned to verify their bid response prior to submission.

Signature.
All bids must be signed by a duly authorized officer of the company empowered with the legal right to bind the company.  A typed name will not be acceptable without the person’s written signature as well. Signatures are required where indicated; failure to comply with this requirement shall be cause for rejection of bid.  All submitted bids must be binding for a period of ninety (90) calendar days from the bid submission deadline. 

Response to Terms and Conditions.
Unless an exception is taken, the awarded contract will contain the requirements of this Request for Proposals.  In its sole discretion, the City reserves the right to either consider or reject any bid which takes exception to the specifications or attached contract. 

Completeness of Request for Proposals (“RFP”).
These documents constitute the complete set of specification requirements and RFP. The bidder is responsible for insuring that all pages and all addenda are received. The City advises all bidders to closely examine this RFP package and immediately direct any questions regarding the completeness of this RFP package and any addenda thereto to the City’s Contact Person.  

Bid Interpretation. Communication with the Purchasing Department
Lisa Lane is the City’s contact for coordinating communications between the department and firms submitting bids.  If additional information is required in order to make an interpretation of items in this RFP, written questions (including faxes or e-mails) will be accepted until ten (10) days prior to the bid opening date.  All questions regarding the RFP should be addressed to:

Lisa Lane, Purchasing Director

200 N. Castle Heights Avenue

Lebanon, TN  37087

Telephone: (615) 443-2802

Email: lisa@lebanontn.org

The City specifically requests that no contact concerning this RFP be made with any other City personnel until the selection process has been completed.  Failure to honor this requirement will be viewed negatively in the selection process and may result in the disqualification of a bid.

Discrepancies, Errors, and Omissions.
Any discrepancies, errors, omissions, or ambiguities in this RFP, the specifications or addenda (if any) should be reported to the contact person for the City.  If necessary, a written addendum will be issued to firms on record and the addendum will be incorporated in the RFP and will become part of the contract.  The City will NOT be responsible for any oral instructions, clarifications or other communications and no such oral communication may be relied on by any bidder. 

Errors.
Certain mistakes may be corrected so long as the intended correct bid response is clearly evident.  In the event of a disagreement between unit price and extended price, the unit price will control. 

Further Negotiation.
The City reserves the right to further negotiate, after the RFPs are opened, with any potential vendor if such is deemed necessary at the discretion of the City.

Economy of Preparation.
RFP should be prepared simply and economically, providing a straightforward, concise description of bidder’s capabilities to satisfy the requirements of the RFP.  Emphasis should be on completeness and clarity of content.

Subcontracting.
If any part of the work is, or is to be, subcontracted, the bidder shall provide within the RFP a description of the subcontracting organization and the contractual arrangements made therewith.  All subcontractors will be subject to approval by the City.  The successful bidder will also furnish the corporate or company name and the names of the officers or principals of said companies proposed as subcontractors by the bidder.

Bid Modification.
Bids may be modified, withdrawn, and/or resubmitted in writing to the City prior to the deadline for bid submission.  After this deadline, no withdrawals or resubmissions may be made for any reason.

Tax Exempt.
The City is exempt from federal and state taxes. Upon request, the City will provide a sales tax exemption certificate to the awarded firm. Contractors doing business with the City shall not be exempted from paying sales tax to their suppliers for materials to fulfill contractual obligations to the City, nor shall any vendor be authorized to use the City’s Tax Exemption Number in securing such materials.

Pricing Effective for One (1) Year.
The successful bidder shall provide in the bid price the cost for services rendered. Pricing shall be effective for one (1) year from date of bid award.  If, in the bidder’s opinion, additional equipment or services are necessary to make the system fully operational, this shall be included with explanation in the bid.  It is requested that bidders raise any such questions in advance of submitting a bid to the City.  To submit a bid implies consent to the terms set forth in this ITB.

Approval Required.
No award or acquisition can be made until approved by the City Council.  The City will not be obligated to bidders for equipment and/or services until the completion of a signed contract approved by authorized officials of the City.  This solicitation in no manner obligates the City to the eventual rental, lease, or purchase of any equipment or services described, implied, or which may be proposed, until confirmed by a written contract.  Progress towards this end is solely at the discretion of the City and may be terminated at any time prior to the signing of a contract.

Consideration of Bid.
Any items proposed deemed not of equal and/or better and of comparable quality as that specified shall be cause for rejection of a bid. In addition to the price, the following aspects will be considered in the award of a contract:

a. The ability of the bidder to perform the contract or to provide the material for service required;

b. Whether the bidder can perform the contract and provide the material or service promptly or within the time specified without delay or interference;

c. The character, integrity, reputation, experience and efficiency of the bidder;

d. The previous and existing compliance by the bidder with laws and ordinances relating to the contract or service;

e. The ability of the bidder to provide future maintenance and service for the use of the subject contract;

f. Terms and conditions stated in bid;

g. Compliance with specifications or the RFP;

h. Utilization of the format set forth in Section 3 for submittal of a bid; and,

i. Bidder’s past performance with the City.

Terms and Conditions.
The City reserves the right to reject any and all bids, to waive any irregularities in a bid, to make awards to more than one bidder, to accept any part or all of a bid, or to accept the bid (or bids) which, in the judgment of the governing body, is in the best interest of the City.  The City also reserves the right to make revisions to any quantity shown on the bid form dependent upon bid prices and available funding.  Prices bid on each item shall be firm regardless of the actual quantity of item(s) purchased. 

Withdrawal of Bid.
No bidder may withdraw its bid for a period of ninety (90) calendar days after the date and time set for the opening of the responses. In the event the City awards a contract to a bidder and during such ninety (90) day period determines that such bidder will be unable to properly perform the contract, the City reserves the right to terminate the contract and award the contract to the next best offer without being required to re-advertise the project.

Cost of Response.
The City will not be liable for any costs incurred by the bidders in preparing a response to this solicitation. Bidders will submit responses at their own risk and expense. The City makes no guarantee that any equipment or services will be purchased as a result of the solicitation and reserves the right to reject any and all responses.  All responses and their accompanying documentation will become the record of the City.

Contract Termination.
The City reserves the right to cancel the contract for the work without cost or penalty to the City if, in the City’s opinion, there is a failure at any time by the contractor to adequately perform the contract, or if there is any attempt to willfully impose upon the City a material or product or workmanship which is, in the opinion of the City, of an unacceptable quality.  Cancellation of the contract shall not impair any rights or claim of the City to damages for the breach of any covenants of the contract by the contractor.   

The contract awarded may be terminated upon any of, but not limited to, the following occurrences: 

a) bankruptcy or insolvency of the bidder or one or more of the bidder’s principal owners; 

b) unauthorized substitution of products other than those identified in the specifications or specifically approved by the City as a substitute prior to award of the contract; 

c) unsatisfactory performance of products supplied by the bidder or services provided by the bidder; 

d) fraud 

e) and any other breach of the terms of the ITB specifications or contract.
Contract Modification.
The contract may be modified only by written amendment executed by all parties and their signatories hereto. 

Replacement or Repair.
No waiver of any provision of the contract shall affect the right of any party thereafter to enforce such provision or to exercise any right or remedy available to it in the event of any other default.

The City, at its option and in lieu of immediate termination, may request the awarded bidder replace or repair any defective goods or correct performance by written notice to the contractor.  In that event, the contractor shall take corrective action within the amount of time specified by the City in the written notice.  Exercise of this option shall not relieve the contractor of any liability to the City for damages for the breach of any covenants of the contract by the contractor.

Expense of Legal Action.
Awarded bidder agrees that, in the event either party deems it necessary to take legal action to enforce any provision of the contract, and in the event the City prevails, awarded bidder shall pay all expenses of such action including the City’s attorney fees and costs at all stages of the legal action.

Governing Laws.
The validity, construction and effect of the contract, and any and all extensions and/or modifications thereof shall be governed by the laws of the State of Tennessee.  

Severability.
Should any provision of the contract be declared to be invalid by any court of competent jurisdiction, such provision shall be severed and shall not affect the validity of the remaining provisions of the contract. Any action between the parties arising from this agreement shall be maintained in the courts of Wilson County, Tennessee. 

Indemnification and Hold Harmless.
Contractor shall indemnify and hold harmless the City, its officers, agents and employees from: i) any claims, damages, costs, and attorney fees for injuries or damages arising, in part or in whole, from the negligent or intentional acts or omission of awarded bidder, its officers, employees and/or agents, including its sub or independent contractors, in connection with the performance of this contract; and ii) any claims, damages, penalties, costs, and attorney’s fees arising from any failure of awarded bidder, its officers, employees and/or agents, including its sub or independent contractors, to observe applicable laws, including, but not limited to, labor laws and minimum wage laws.

Statutory Disqualification.
By submitting a response, it is represented that neither it nor any of its officers, directors, shareholders, member, or partners has been convicted or plead guilty or nolo contender to any violation of the Sherman Anti-Trust Act, mail fraud, or other state or federal criminal violation in connection with a contract let by the City of Lebanon or any political subdivision of the State of Tennessee.

Contractor’s Employment Practices.
Bidder, after being first duly sworn, affirms that by its employment policy, standards and practices, it does not subscribe to any personnel policy which permits or allows for the promotion, demotion, employment, dismissal or laying off of any individual due to the individual’s race, creed, color, national origin, age or sex and it is not in violation of and will not violate any applicable laws concerning the employment of individuals with disabilities.

City’s Employment Practices.
It is the policy of the City not to discriminate on the basis of age, race, sex, color, national origin, or disability in its hiring and employment practices, or in admission to, access to, or operation of its programs, services, and activities. With regard to all aspects of this contract, Contractor certifies and warrants it will comply with this policy.

Conflict of Interest.
By submitting a response, it is represented that no officer, committee member, or director of the City or other persons whose duty is to vote for, let out, overlook, or in any manner supervise any work on any contract for the City has a “direct interest”, as defined by T.C.A. §12-4-101, in the bidder or in the work which is subject to this ITB.

Ethical Standards.
Bidder understands that it shall be a breach of ethical standards for any person to offer, give or agree to give any employee or former employee, or for any employee or former employee to solicit, demand, accept or agree to accept from another person, a gratuity or an offer of employment in connection with any decision, approval, disapproval, recommendation, preparation of any part of a program requirement or a purchase request, influencing the content of any specification or procurement standard, rendering of advice, investigation, auditing or in any other advisory capacity in any proceeding or application, request for ruling, determination, claim or controversy or other particular matter, pertaining to any program requirement of a contract or subcontract or to any solicitation or bid therefore.

Breach of Ethical Standards.
A breach of ethical standards could result in civil and/or criminal sanctions and/or debarment or suspension from being a contractor or subcontractor under City contracts.

Payments.
Payments under the contract shall be made upon submittal of an invoice after performance of the portion of the services which each payment represents.  The final payment shall not be made until after the performance is complete.

Codes & Regulation.
All services and/or equipment must comply with city, county, state, and federal laws, rules, codes and regulations.  The contractor will obtain and pay for all permits, if any, necessary to complete the work.

Bid Modification & Registration
Bids may be modified, withdrawn, and/or resubmitted in writing to the City prior to the deadline for bid submission.  After this deadline, no withdrawals or resubmissions may be made for any reason. 

Iran Divestment Act of Tennessee

              By submission of this bid, each bidder and each person signing on behalf of any bidder  

certifies, and in the case of a joint bid each party thereto certifies as to its own  

organization, under penalty of perjury, that to the best of its knowledge and belief that   

each bidder is not on the list created pursuant to §12-12-106. Bids not conforming with this   provision shall not be opened.  Failure of any bidder to comply therewith shall void such bid and such bid shall not be considered.

QUANTITY
DESCRIPTION

UNIT COST

TOTAL
4 

Backwash Actuators 





$_____________
$_____________

1

Parts &Labor

$_____________
$_____________

1

Shipping Charges

$_____________
$_____________

1

Total



$_____________
$_____________
3. WARRANTY 

Bidders shall state the warranty period on the bid pricing form.  

4. INSTALLATION
The vendor must state their expected installation date. 

5. EXCEPTIONS

The above are minimum specifications.  If there are any exceptions to these specifications, please make any notations to the right of that spec. and the exceptions will have to be approved by the department.  

6. BID PRICE

TOTAL BID $_______________________

     
6.2    INSTALLATION   _____________________

Company Name and Authorized Representative

______________________________________________________________

Address and Contract Phone Number

Include:

Proof of Liability Insurance, Worker’s Comp., Contractor’s License, Business License.
2

