Tryon Library HVAC Systems Replacement Scope of Work

Location: 	Tryon Branch Library

1200 Langley Avenue

Pensacola, FL 32504

This scope of work is for the removal and replacement of the five (5) HVAC systems at the above listed location. The systems currently installed are as follows:

HP-1	York Condenser	Model# EA090C00A2AAA1A		Serial# N0M8478607

York Air Handler	Model# FA090C00A6AAA1B		Serial# N0K8330768

Aux Heater		Model# 2HS04501025A		Serial# SN849311

HP-2	York Condenser	Model# EA090C00A2AAA1A		Serial# N0M8457815

York Air Handler	Model# FA090C00A6AAA1A		Serial# N0L7405883

Aux Heater		Model# 2HS04500125A		Serial# SN849311

HP-3	York Condenser	Model# EA120C00A2AAA1A		Serial# N0L7348647

York Air Handler	Model# FA120C00A6AAA1A		Serial# N0K7244670

Aux Heater		Model# 2HS04501025A		Serial# SN849311

AC-1	York Condenser	Model# H1RA076S25H		Serial# W0N8493320

York Gas Furnace	Model# GY8S160E30UH21D		Serial# W0M8449939

ADP Evaporator	Model# G2FD0090S35A		Serial# 7108H20042

AC-2	York Condenser	Model# H1RA076S25H		Serial# W0N8493317

York Gas Furnace	Model# GY8S160E30UH21D		Serial# W0M8449936

ADP Evaporator	Model# G2FD0090S35A		Serial# 7108H20041

All systems must meet the following specifications:

- All systems, if possible, need to be two stage single refrigerant circuit.

- All systems must be at least 11eer or better.

- All 7.5tn and 10tn air handlers must be belt driven blower with VFD.

- All evaporator coils must have factory installed TXV or EEV.

- All systems to be R-410A refrigerant.

- All condensers must have high and low pressure protection installed.

- All gas furnaces must be at least 80% efficient with two stage gas valves.

- All gas furnaces must have ECM blower motors.

- All systems must have thermostats equipped with humidity sensor and must be able to control space humidity levels at between 40%-60%.

- All three phase equipment must have phase monitoring and phase loss protection installed.

All systems must meet the following installation specifications:

- All work must be permitted and inspected, and installed to meet or exceed local, state, and federal codes that apply.

- All systems will be installed per manufacture specifications to ensure full factory warranty.

- All existing smoke detectors will be reconnected to new systems and function as intended.

- All condensers must be secured to existing slab as per code.

- All ductwork that must be modified or replaced to attach to new systems must be sealed with tape and mastic.

- All insulation removed or required for new ductwork must be at least R-6 and must be sealed with tape and mastic to prevent condensation on ductwork.

- All suction lines to condensers, air handlers, and evaporator coils must be at least ¾” wall insulation, and all joints or seams must be glued with appropriate contact adhesive designed for rubber tubing insulation.

- All drain lines must be either copper or schedule 40 PVC and installed as per manufacture recommended specifications.

- All drain lines must be insulated with at least ½” wall insulation, and all joints and seams must be glued with appropriate contact adhesive designed for rubber tubing insulation.

- All drain lines must have safety switches installed to shut units down incase of blockage in drain line.

- All drain lines must be securely fastened to floor and routed to nearest floor drain.

- All air handling units must have anti-vibration pads installed under units.

- Carbon monoxide detectors must be installed in mechanical room near gas furnaces.

- All vent piping for gas furnaces must be of appropriate size and configuration as per code.

- Appropriately sized Ionic style air cleaners must be installed in systems.

Contractor must provide all needed electrical, copper, refrigerant, labor, and any other required materials needed to install and make systems fully operational.

Contractor is responsible for removal and disposal of all removed equipment and accessories.

Contractor must keep job site clean and all proper safety procedures must be followed during installation.

Contractor must install appropriately sized pleated filters on startup of new systems and at least one full set of filters to Escambia County Facilities for first scheduled filter change.

All work must be inspected by Escambia County Facilities Management representative and any punch list items resolved before invoice is submitted for payment.

Contractor must provide a minimum of a 90-day parts and labor warranty from date of job completion.

Contractor must provide all IOM documents on all installed equipment, including thermostats, Ionic air cleaners, phase monitors, and carbon monoxide detectors.

Contractor is responsible and must provide documentation showing all installed equipment and accessories are registered with manufactures for full factory warranty.

Contractor site visit is scheduled for March 17th, 2022 at 1:00pm.

This is not a mandatory site visit, but attendance is encouraged due to location of condensing units and constraints of current refrigerant line installation.

Bids will be due by end of day on March 25th, 2022.

Escambia County Facilities Contact Information:

William (Bill) Barrett

wcbarrett@myescambia.com

Cell# 850-554-2726

Office# 850-595-3878