Daphne Utilities

Marinda Turner, Buyer

251-210-1647 Office

marinda@daphneutilities.com

| Request for Bid no.: | RFB 20-04 |
| --- | --- |
| Name of bid: | Storage Tank 3,000 gallon |
| Contact person: | Marinda Turner 251-210-1647 Larry English 251-583-5643 (technical information) |

Bid Specifications

FRP 0.8% Sodium Hypochlorite Storage Tank

Tank is to be designed for storage of 0.8% Sodium Hypochlorite, at specific gravity 1.2, ambient temperature and atmospheric pressure. Withstand 105 mph winds, 3 ft uplift condition and seismic conditions in accordance with IBC 2009. Tank will be outdoors. Tank will be manufactured per ASTM D-3299 and ASTM D-4097 specifications from Hetron FR992 vinyl ester resin throughout with double C-veil liner with BPO-DMA cure.

- 3,000 gallon

- 8’ diameter x 8’ straight side height

- Vertical

- Flat bottom

- Dome top

- Single wall

- Fiberglass tank

Tank to include the following:

- 1 – 24” top manway with Viton gasket and 316 ss bolts

- 3 – 3” flanges with conical gussets

- 1 – 3” fiberglass J-vent assembly

- 1 – 2” flange with conical gusset

- 1 – 2” double flange with conical gusset

- 2 – 1” flanges with conical gussets

- 1 – 1” clear PVC sight gauge assembly with wind guards

- 1 – 2” foam insulation with 100 mil fiberglass overcoat

- 1 – fiberglass ladder

- 4 – 316 ss lifting lugs and tie down lugs

- Hydro test

- Post cure

- Stainless steel nameplate with bracket support

Freight costs for delivery to Daphne Utilities Water Quality Plant, 28340 County Road 13, Daphne, Alabama 36526 shall be included as a separate item and should be a firm cost.