Daphne Utilities

Generators

RFB 21-12

Bid Specifications

The scope of work shall consist of supplying and installing one 200 Kw natural gas generator and two (2) 60Kw natural gas generators according to the following specifications:

Generator at Central Water Treatment Plant – 200 Kw on natural gas, EPA stationary standby, 480/277VAC, 3 phase, 60 Hz

Location – 8201 Well Road, Daphne, Alabama 36526

- Engine

  - Model - 11.1L Natural Gas

  - BMEP: natural gas: psi (kPa)197 (1358.3)

  - Gross horsepower: natural gas 288

  - Heavy duty air cleaner with service indicator

  - 50° C ambient radiator

  - Electronic isochronous governor with 0.5% frequency regulation

- Alternator

  - Model – UC1274J311

  - 277/480 voltage with 840 sKVA at 30%

  - 1.0% AVR, PMG

  - Brushless rotating field generator with Class H insulation

  - Tropical coating

- Circuit breaker

  - 400 Amp , L-frame, 100% rated, electronic (LI), main line circuit breaker

- Control Panel

  - Open source non-proprietary controller

  - Digital genset controller for integrated engine-genset control, protection, and metering in a single package

  - Front panel controls and indicators

  - Wide temperature-range liquid crystal display (LCD) with backlighting

  - Manual key override by-pass switch

- Heavy duty integral vibration isolators between engine/alternator and base

- 2” NPT inlet connection

- Oil drain kit (oil drain piped to edge of skid with valve)

- Coolant drain kit

- Lube oil and antifreeze (initial fill)

- Battery rack and cables

- Flex fuel line

- 120V, 2500W block heater with valves

- 10 Amp/24 Volt battery charger

- Two 12Volt lead acid battery, 1100CCA

- Standard weather proof enclosure with internal critical silencer and stainless flex

  - Heavy duty 14 gauge steel

  - Peaked roof

  - Lockable doors

  - Stainless steel hinges and hardware

  - Powder coat finish

- One hour factory load bank test

- Start up included at site after complete installation by others (one trip)

- Standard 2 year standby limited warranty

- One electronic O&M manual

- Certified to UL2200

- Delivery to site included. Off loaded by Daphne Utilities personnel

Daphne Utilities

Generators

RFB 21-12

Generator at Well #3 and generator at Well #8 – 60 Kw on natural gas, EPA stationary standby, 480/277VAC, 3 phase, 60 Hz

Location – Well # 3 at the end of Jackson Way, Daphne, Alabama 36526 and Well #8 at the corner of Public Works Road and Well Road, Daphne, Alabama 36526

- Engine

  - Model - 5.7L Natural Gas

  - Gross horsepower: natural gas 104.7

  - Heavy duty air cleaner with service indicator

  - 50° C ambient radiator

  - Electronic isochronous governor with 0.5% frequency regulation

- Alternator

  - Model – UC1224F311

  - 277/480 voltage with 257 sKVA at 30%

  - 1.0% AVR, PMG

  - Brushless rotating field generator with Class H insulation

  - Tropical coating

- Circuit breaker

  - 90 Amp , L-frame, 100% rated, electronic (LI), main line circuit breaker

- Control Panel

  - Open source non-proprietary controller

  - Digital genset controller for integrated engine-genset control, protection, and metering in a single package

  - Front panel controls and indicators

  - Wide temperature-range liquid crystal display (LCD) with backlighting

  - Manual key override by-pass switch

- Heavy duty integral vibration isolators between engine/alternator and base

- 2” NPT inlet connection

- Oil drain kit (oil drain piped to edge of skid with valve)

- Coolant drain kit

- Lube oil and antifreeze (initial fill)

- Battery rack and cables

- Flex fuel line

- 120V, 1500W block heater with valves

- 6 Amp/12 Volt battery charger

- One 12Volt lead acid battery, 950CCA

- Standard weather proof enclosure with internal critical silencer and stainless flex

  - Heavy duty 14 gauge steel

  - Peaked roof

  - Lockable doors

  - Stainless steel hinges and hardware

  - Powder coat finish

- One hour factory load bank test

- Start up included at site after complete installation by others (one trip)

- Standard 2 year standby limited warranty

- One electronic O&M manual

- Certified to UL2200

- Delivery to site included. Off loaded by Daphne Utilities personnel

The vendor must comply with standard record keeping and reporting requirements. Payment will be made by Daphne Utilities after the goods and services have been received, accepted, and properly invoiced with the purchase order number.  Any defects in the work performed or product delivered must be corrected before invoices are eligible for payment. Payment terms shall be net 30 days.

Daphne Utilities

Generators

RFB 21-12

Bid Form

Generator 200Kw at Central Water Treatment Plant	$______________

Estimated lead time	______________

Generator 60Kw at Well #3	$______________

Estimated lead time	______________

Generator 60Kw at Well #8	$______________

Estimated lead time	______________

I have read and understood the terms and conditions and the bid specifications of this bid.  I also understand, and have provided or will provide at the appropriate time, all documentation required.  Omission of any required documentation may result in the bid being deemed unresponsive by Daphne Utilities.

Submitted by: __________________________________________________________			        Company name of bidder

_________________________________________________________________________________________

By:  company officer name

_________________________________________________________________________________________

Signature

__________________________________________		________________________________		Title							Date

_________________________________________________________________________________________

Company address, city, state, zip

___________________________________________		________________________________

Phone							EIN / tax id number

___________________________________________		________________________________

Point of contact name					Point of contact phone

___________________________________________

Point of contact email