BID 22-22 – HVACR PM MAINTENANCE/FILTER CHANGE

EXHIBIT B

EQUIPMENT TASK LIST

BASE MOUNTED CIRCULATING PUMP

| PART | ###### TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Gauges | When available, check/record suction and discharge pressures. | Q |
| Base | Check pump mounts for tightness/wear – Inspect for corrosion – clean pump exterior & check for corrosion on pump exterior and base plate – clean area around base and pad. | Q |
| Motor | Inspect coils & contacts – check current to motor – perform vibration test – lubricate bearings. | S |
| Coupling | Check for proper alignment – inspect wear – inspect shaft – realign. | Q |
| Impeller | Listen for proper operation. | Q |
| Housing | Check packing & seals for leaks – inspect gaskets – lubricate drive shaft bearings. | Q |
| Suction/discharge piping/valves | Check for leaks on gaskets, seals, packing glands, etc., - make minor adjustments as required – when available, check suction and discharge pressure gauge readings and flow rate. | Q |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

##### IN LINE CIRCULATING PUMP

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, makes model, voltage, amperage, capacity, etc.).) – denote any changes from last inspection. | A |
| Gauges | When available, check/record suction and discharge pressures. | Q |
| Motor | Inspect mounting brackets & bolts – lubricate motor bearings – check for excessive vibration, noise and overheating. | S |
| Impeller | Listen for proper operation. | Q |
| Coupling | Check for proper alignment – inspect for wear – inspect shaft – realign– check for excessive vibration, & noise. | Q |
| Housing | Check packing & seals for leaks – inspect gaskets – lubricate drive shaft bearings – clean pump exterior and check for corrosion. | Q |
| Suction/discharge piping/valves | Check for leaks on gaskets, seals, packing glands, etc., - make minor adjustments as required. | Q |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22-- Exhibit B

Equipment Tasklist

PLATE EXCHANGER

| PART | # TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, model, voltage, amperage, capacity, etc.).) – denote any changes from last inspection. | A |
| Shell | Inspect for leaks – paint when required – inspect air vent. | S |
| Tubes | Clean & inspect – check for leaks or water hammer damage. | Q |
| Control Valve | Check for proper operation – replace valve when needed – lubricate and reseat. | Q |
| Inlet and Outlet | Inspect for leaks – tighten connections. | S |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

UNIT VENTILATOR

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Dampers | Lubricate bearings – Tighten linkages – check for proper operation. | S |
| Filters | Inspect for damage – clean or replace. | Q |
| Heating Coil | Clean surfaces – comb bent fins – check for leaks or damage. | S |
| Supply Fan | Clean and inspect – check rotation of shaft – Lubricate bearings. | S |
| Motor | Clean and inspect – lubricate bearings – tighten motor mounts and brackets. | A |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

WATER COOLED HEAT PUMP

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, make model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Controls | Test for proper operation – tighten all connections – test for sequence of operation. | A |
| Filter section(s) | Check/clean/replace filters. Every 3 months. Clean return air grills. | Q |
| Strainers, piping, flex connections | Check for leaks on piping – clean strainers, check water flow. | S |
| Inside coil | Inspect & clean with coil cleaner – comb bent fins – check for leaks – check/clean drain line & drain pan – perform ELECTRONIC refrigerant leak inspection. | AR |
| Outside coil | Inspect and clean – comb bent fins – perform ELECTRONIC refrigerant leak test. | AR |
| Condenser | Backflush condenser to remove any sediment. | Q |
| Compressor | Check/verify compressor safety control operation - check for oil leaks – check crankcase heater for proper operation – check amp draw of compressor– perform ELECTRONIC refrigerant leak inspection. DO NOT CHECK REFRIGERANT CHARGE. | S |
| Motor-Outside Fan & Supply Fan | Inspect and clean – check for proper rotation – check motor shaft & lubricate if needed– check belts for proper tension and alignment, adjust as needed – replace annually, check for bent blades or unbalance. | A |
| Reversing valve | Cycle reversing valve to insure proper operation. | Q |
| Metering Device | Check for proper operation – adjust and calibrate – check for leaks. | Q |
| Dampers | Check and lubricate dampers, if applicable. | A |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, make model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | S |
| Fan motor(s) | Inspect motor mounts & tighten – inspect coils and contacts – tighten electrical connections – lubricate as required by factory specifications. | AR |
| Fan(s) | Check fan for alignment – check shaft for alignment – check all belts/couplings – align couplings – tighten mounting bolts. | A |
| Belts | Check belts for wear, proper tension, alignment, and adjustment – replace annually. | S |
| Condenser coil | Clean/Pressure wash all surfaces – comb bent fins – check for leaks – check for vibrations – verify heat rejection capacity of condenser. | AR |
| Frame | Check for damage – clean surface – treat for corrosion – tighten all bolts. | AR |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

### COOLING TOWER

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Basin | Inspect for corrosion – clean surfaces. | A |
| Eliminators | Inspect for wear – inspect for corrosion. | A |
| Fan | Check blades for alignment – clean dirt from blades – lubricate bearings – check couplings. | S |
| Belts | Check belts for wear, proper tension, alignment, and adjustment – replace annually. | S |
| Baffles | Inspect for corrosion or damage – inspect for wear. | A |
| Sump | Clean sump & inspect for corrosion. | A |
| Water inlet & outlet | Inspect and check for leaks. | S |
| Overflow | Clean overflow – check for corrosion. | A |
| Float valve | Check for proper operation – clean and test for cut off. | S |
| Drain | Inspect for blockages – check proper shut off. | A |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

### SELF CONTAINED AIR CONDITIONING UNIT (SPLIT SYSTEM)

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Compressor | Check for oil & refrigerant leaks – check crankcase heater. | S |
| Condenser fan | Clean & inspect – lubricate bearings – tighten motor mounts. | S |
| Condenser coil | Clean/Pressure wash coil – comb bent fins – check for leaks. | A |
| Control panel | Sequence operation – tighten connections. | A |
| Supply fan | Clean and inspect – check fan rotation – check shaft & bearings. | S |
| Supply fan motor | Clean & inspect – lubricate motor & bearings – tighten motor mounts. | S |
| Heating & cooling coil | Inspect & clean surfaces – comb bent fins – Perform ELECTRONIC refrigerant leak inspection on cooling coil. | S |
| Filters | Clean and/or replace as required. Clean return air grill. | Q |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

### ROOFTOP HVAC UNIT

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Filter section(s) | Check/clean/replace filters. Clean return air grills. | Q |
| Filter section(s) Fresh Air Intake Metal Filters | Check/clean/filters. | Q |
| Fresh air damper (economizer) | Check for proper operation – lubricate bearings. | A |
| Return air damper | Check for proper operation – lubricate bearings. | A |
| Exhaust air damper | Check for proper operation – lubricate bearings. | A |
| Return and supply fans | Lubricate bearings – check for bearing wear – clean dirt accumulation – check drive couplings, tighten. | S |
| Belts | Check belts for wear, proper tension, alignment, and adjustment – replace annually. | S |
| Electrical & disconnect | Inspect & clean contacts – check for proper operation – clean dirt accumulation – inspect & tighten electrical connections verify proper operation of all electrical components & record amperages. | S |
| Condenser fan | Lubricate bearings – check for bearing wear – check drive coupling and belts –adjust tightness of belts. | S |
| Condenser coil | Clean fin surfaces – comb bent fins – check for leaks – check for corrosion – perform ELECTRONIC refrigerant leak inspection. | S |
| Cooling coil | Inspect & clean surfaces with coil cleaner – comb bent fins – perform ELECTRONIC refrigerant leak inspection. | A/AR |
| Controls | Check/and Cycle operating controls. | A |
| Compressor | Check/verify compressor safety control operation – check crankcase heater – check for oil leaks – check oil level – check for vibration – observe operating temperatures. | A |
| Refrigerant Charge | Verify refrigerant charge, suction and head pressures – confirm operation of unloaders - perform ELECTRONIC refrigerant leak inspection. | S |
| Heating section | Inspect & clean – check for corrosion – check for leaks – perform carbon monoxide testing on supply side of heat exchanger. | S |
| Temperatures | Record all temperatures. | A |
| Panels & doors | Secured properly. | Q |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

### MAKE-UP AIR UNIT/ ENERGY RECOVERY UNIT

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Filter section(s) | Check/clean/replace filters. | Q |
| Filter section(s) Fresh Air Intake Metal Filters | Check/clean/filters. | Q |
| Fresh air damper (economizer) | Check for proper operation – lubricate bearings. | A |
| Return air damper | Check for proper operation – lubricate bearings. | A |
| Exhaust air damper | Check for proper operation – lubricate bearings. | A |
| Return and supply fans | Lubricate bearings – check for bearing wear – clean dirt accumulation – check drive couplings, tighten – check belts – check alignment of shaft – check fan blade tightness. | A |
| Belts | Check belts for wear, proper tension, alignment, and adjustment – replace annually. | S |
| Electrical & disconnect | Inspect & clean contacts – check for proper operation – check electrical reheat for proper operation - clean dirt accumulation – inspect & tighten electrical connections verify proper operation of all electrical components & record amperages. | S |
| Condenser fan | Lubricate bearings – check for bearing wear – check drive coupling and belts –adjust tightness of belts. | S |
| Condenser coil | Clean fin surfaces – comb bent fins – check for leaks – check for corrosion – perform ELECTRONIC refrigerant leak inspection. | S |
| Zone control actuators | Inspect for proper operation – clean surfaces. | A |
| Controls | Check/and Cycle operating controls. | A |
| Heat wheel | Check for proper operation – check belt(s) – check, lubricate bearings as needed. | Q |
| Cooling coil | Inspect & clean surfaces with coil cleaner – comb bent fins – perform ELECTRONIC refrigerant leak inspection. | A/AR |
| Compressor | Check/verify compressor safety control operation – check crankcase heater – check for oil & refrigerant leaks – check oil level – check for vibration – observe operating temperatures – verify refrigerant charge, suction and head pressures – confirm operation of unloaders - perform ELECTRONIC refrigerant leak inspection. | A |
| Burner section | Perform draft & combustion test – clean & inspect nozzles –clean and inspect blower – lubricate blower motor – test safety controls. | S |
| Heating section | Inspect & clean – check for corrosion – check for leaks – perform carbon monoxide testing on supply side of heat exchanger. | S |
| Temperatures | Record all temperatures. | A |
| Panels & doors | Secured properly. | Q |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

AIR HANDLING UNIT

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Dampers | Lubricate bearings – check for proper operation – adjust & calibrate – clean surfaces – tighten connections. | A |
| Filters | Clean and/or replace as required. Clean return air grills. | Q |
| Heating & cooling coils | Clean coils, evaporator drain pan & condensate lines – comb bent fins – - perform ELECTRONIC refrigerant leak inspection on cooling coil – inspect for corrosion. | A |
| Motor | Check for vibration – tighten electrical connections – tighten mountings – lubricate motor – check for unusual noise or vibration. | Q |
| Controls | Inspect contacts & starter – Check controls for proper operation. | A |
| Fan | Clean & inspect – lubricate bearings - check for vibrations –check fan rotation– check for unusual noise or vibration. | S |
| Belts | Check belts for wear, proper tension, alignment, and adjustment – replace annually. | S |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

EXHAUST FAN

| PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Fan | Check shaft & bearings for noise and vibration – lubricate as required. | S |
| Motor | Check shaft & bearings for noise, vibration and overheating lubricate as required. | S |
| Belts | Check belts for wear, tension & alignment – adjust/replace annually. | S |
| Electrical | Check connections –tighten loose connections. | S |
| Cleanliness | Clean fan and surrounding area. | S |
| Filters | Change filters. | N/A |
| Dampers, louvers, & shutters | Check for wear – lubricate all pivot points and linkages as necessary. | S |
| Piping | Check exterior piping and valves for leaking – tighten as required. | S |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

WATER COOLED CHILLER

| # PART | # TASK | # FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Electrical | Check/inspect & tighten all electrical connections – record amperages – verify proper operation of all electrical components – test system flow switches – cycle operating controls – check chiller safety controls. | Q |
| Refrigerant circuits | Perform ELECTRONIC refrigerant leak inspection – verify refrigerant charge, suction & head pressures, report findings to the Division of Maintenance. | Q |
| Compressor(s) | Confirm operation of unloaders – check refrigerant oil level in all compressors, DO NOT adjust oil levels – verify crankcase heater operation. | Q |
| Chiller water circuit | Record temperatures – check water flow of evaporators and condensers – check vibration eliminators – check chilled water Delta T. | Q |
| Condenser water circuit | Check all fitting, valves, gauges, and gaskets for water leaks – check/clean strainer. | Q |
| Condenser | Verify heat rejection capacity of condensers. | Q |
| Drives & couplings | Check alignment of drives and couplings. | Q |
| Chiller | Check operation of unit through entire cycle. | Q |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

AIR COOLED CHILLER

| # PART | # TASK | # FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (serial number, model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Electrical | Check/inspect & tighten all electrical connections – record amperages – verify proper operation of all electrical components – test system flow switches – cycle operating controls – check chiller safety controls. | Q |
| Refrigerant circuits | Perform ELECTRONIC refrigerant leak inspection – verify refrigerant charge, suction & head pressures, report findings to the Division of Maintenance. | Q |
| Compressor(s) | Confirm operation of unloaders – check refrigerant oil level in all compressors, DO NOT adjust oil levels – verify crankcase heater operation. | Q |
| Chiller water circuit | Record temperatures – check water flow of evaporators and condensers – check vibration eliminators – check chilled water Delta T. | Q |
| Condenser | Verify heat rejection capacity of condensers – clean/pressure wash air-cooled condenser coils. | S/AR |
| Drives & couplings | Check alignment of drives and couplings. | Q |
| Chiller | Check operation of unit through entire cycle. | Q |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

AIR COOLED CONDENSER

(PORTABLE CLASSROOM)

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, make model, voltage, amperage, capacity, etc.) – denote any changes from last inspection. | A |
| Controls | Verify proper operation of all controls – inspect & tighten electrical connections as required - test system flow switches when required – cycle operating controls – check/verify compressor safety controls. | Q |
| Fan motor(s) | Inspect motor mounts & tighten – inspect coils and contacts – tighten electrical connections – lubricate as required by factory specifications. | AR |
| Fan(s) | Check fan for alignment – check shaft for alignment – check all belts/couplings – align couplings – tighten mounting bolts. | A |
| Filters | Change filters. Clean return air grills. | Q |
| Condenser coil | Clean/Pressure wash all surfaces – comb bent fins – check for leaks – check for vibrations – verify heat rejection capacity of condenser. | AR |
| Frame | Check for damage – clean surface – treat for corrosion – tighten all bolts. | AR |
| Checklist /report | Fill out maintenance checklist and report deficiencies. | AR |

Bid 22-22 -- Exhibit B

Equipment Tasklist

DAIKIN INDOOR/ OUTDOOR UNITS

| # PART | TASK | FREQUENCY |
| --- | --- | --- |
| Nomenclature | Record/Verify Equipment ID numbers (manufacturer, serial number, make model, voltage, amperage, capacity, etc.) – denote any changes from last inspection | AR |
| Filters | Daiken VRV facilities have factory filters that require cleaning (washing, cleaning and reinstalled) every 60 days. Disposable filters shall not be used on VRV systems. | Bi Monthly |
| Coil | Inspect/Verify coil is clean and clear of any debris/clean coil as required | Bi Monthly |