Request For Proposals

Saginaw Public School District

Saginaw Arts & Sciences Academy

1903 N. Niagara St., Saginaw, MI 48602

HVAC Compressor Replacement

Summary

Replace two existing compressors associated with rooftop condensing unit #3.

Trane

Model# RAUBC604EE00B1

Serial# J87E81269

Compressors

Model # CRHK300C40A0R

Scope of Work

Furnish and install:

2 – New compressors, 460V/60Hz/3PH

2 – Contactors 3PH/60A/120VAC/Lugs

2 – Switch, AUX, 1 NO / 1 NC, for 20A-60A

Perform Acid Test and Recovery of existing refrigerant (R-22). Acid test to be recorded in service report.

Install all new associated filter/driers including suction driers if needed for acid removal (if acid is present system is to be flushed and filter/driers changed).

Pressurize lines with Nitrogen to perform leak testing and repair any leaks found.

Perform an acceptable vacuum procedure to ensure system has no leaks prior to start-up. 500 Microns or less with a 24-hour hold. This must be recorded in service report.

Utilize factory recommended system flushing according to refrigerant manufacturer specifications and charge with R-422D.

Perform start-up and testing to ensure optimal performance.

If any unforeseen issues shall arise that will incur any additional charges above the proposal amount, work shall cease and changes must be negotiated between the contractor and representatives of the Saginaw Public School District.