CITY OF SPRINGFIELD, TENNESSEE

WATER\WASTEWATER DEPT.

INVITATION TO BID

BID NO. 938
2 (Two) Portable Generators:
GENERAL: All equipment furnished shall be new or used. Bidder must meet the minimum standards established by this specification sheet.  Failure to meet these minimum specifications shall cause the bid to be subject to rejection for nonconformity to specifications. All deviations whatsoever must be fully explained on a separate sheet or it will be assumed that the features and performance are as specified without exception.  Failure to deliver unit as proposed and described will result in rejection of the unit.
All specifications are a minimum.
Generators shall comply with the following specifications:

Portable trailer mounted.

Tandem axle with electric brakes

Have less than 3,000 hours of engine running time.
Standby rating 100 ekW (125 kVA)   

Prime rating 90 ekW (112.5 kVA)   

Frequency 60 Hz  
Switchable voltage output:

480/277V 3 phase

208/120V 3 phase

240/120V 1 phase

Convenience receptacles

Hinged door over main connectors

NEMA 1 steel enclosure, vibration isolated

4 cylinder turbo charged diesel engine

EPA Tier 3 Certified for non-road applications.

Engine block (coolant) heater 110-120V
Large fuel tank that will provide a minimum of 24 hours of running time.

A strobe mounted on top and wired to run anytime the engine is running.
A 3” pintle hitch, fenders and a single jack
All taillights, turn signals and safety chains on the generator shall be DOT compliant.

DOT conspicuity tape on all sides of generator
Notes:
Bidder shall supply documentation that a load test was performed during the months of April or May 2015 and that all protective devices, control functions and the system were checked and have passed minimum tests.
The bidder shall maintain a store or branch within 75 miles of the City of Springfield, with provisions for repairing or the supply of parts and be able to obtain parts from the manufacturer within a reasonable length of time.

All units shall be furnished with a 5-year/3,000 hours factory (extended) warranty effective on the date of purchase of the proposed equipment by the City of Springfield.  Bidder shall supply printed specifications, advertising literature, and photographs of the unit(s) it proposes to furnish.

Bidder shall supply:  one (1) parts book, one (1) comprehensive factory service and repair manual, and one (1) operator’s manual for each generator.
Ownership history, maintenance history, and repair history records shall be provided on all used equipment.
All generators that are bid will be examined by city personnel before the bid is awarded, to determine if the generator(s) will suit the needs of the Springfield Water and Wastewater Department and to what extent they meet the specifications.
The city will choose the option that is considered in its best interests.
The bid price shall include all costs, including delivery of the generator(s) to the City of Springfield

Generators are to be delivered to the Springfield Water and Wastewater Department, 924 Central Avenue, Springfield, Tennessee 37172

Any questions regarding these specifications can be directed to either:  Jamie Jackson at the Springfield Water and Wastewater Department at 615-382-1600 or by e-mail at jjackson@springfield-tn.org or Terry Cadwell at the Springfield Water and Wastewater Department at 615-382-1600 or by e-mail at (tcadwell@springfield-tn.org)
BID NO. 938
BID FORM

Approximate delivery time, in days, from date of award: __________________________
Equipment proposed complies with specifications? : ______ Yes _____ No  If “No”, provide an explanation on additional sheets for each deviation.
Manufacturer of generator:

___________________________________________

Year and model: 




___________________________________________

Location of generator:



___________________________________________
TOTAL BID PRICE: 


___________________________________________
DEALER: 





___________________________________________
CONTACT PERSON (print): 

___________________________________________
SIGNATURE: 




___________________________________________
PHONE: 





___________________________________________
NOTE: Fill in all blanks.  The City will choose the option that is considered in its best interests.

PAGE  
1
4/16/2015

