Escambia County Chiller Preventative Maintenance/Service Contract Questions/Responses

Inspection reports from the last 12 months:  Have not received any inspection reports since 4/2021.

The most recent Eddy current reports: Have no record of last time this was performed.

The most recent oil analysis reports: Have not seen any reports on oil analysis.

Once the contract is issued, how much time will the County allow the HVAC Contractor for discovery of any pre-existing repairs? Awarded vendor will be given 30 days after start of contract to identify any pre-existing issues. All known pre-existing issues will be disclosed during mandatory walkthrough. All new “pre-existing” issues will be looked at on a case-by-case basis by Escambia County Facilities Management.

Is the HVAC Contractor responsible under agreement for ALL Chemical Water Treatment of the Cooling Towers and associated equipment? If yes, who is the Current Water Treatment provider? Yes, the awarded vendor will be responsible for ALL chemical water treatment of the cooling towers and associated equipment. Currently, Kurita America Inc. is handling the M.C. Blanchard Building. Triple Point is doing the chillwater at One Stop and the condenser water and the chillwater at the Escambia County Road Prison. At this time, I am not sure if or who the Central Energy Plant chillwater is being treated by.

Does the Agreement include ALL replacement Labor and Parts that are failed or broken (Motors, Compressors, Bearings, Electrical Contactors, Belts, Pulleys, Shafts, etc.) and vehicle and travel costs? Yes, this is an all-inclusive preventative maintenance and service contract. Any parts failure that is not included the listed vendor responsible items must be quoted for replacement. These items will be taken and reviewed on a case-by-case basis. Items that fail under normal conditions and wear items will be the vendors responsibility under the terms of the contract. Under the terms stated in the scope of work these listed parts are to be inspected monthly and replaced as needed.

Will the County clarify equipment failure events due to “Acts of God”, power outages and surges, and owner operator negligence? During any predictable weather event, such as a hurricane, where practical, the equipment under either direction or by the vendor will be properly powered down to minimize any damages. After the event is concluded and the site is safe the equipment will be restarted either under the direction or by the vendor. Where this is not feasible, such as the Escambia County Road Prison, due to site being operational 24/7 365 all precautions will be enacted to ensure minimal harm is done to equipment. In the case of unforeseen power outages that are beyond any human control the vendor will be notified immediately and this will be considered an emergency call and the vendor is required by the terms of the contract to respond within the required two (2) hour window. Vendor will be informed if power is restored before representative is onsite and appropriate course of action will be discussed by vendor and Escambia County Facilities to determine if equipment is safe to restart. Any failure that is deemed to be caused by owner/operator negligence will be repaired or replaced at the expense of Escambia County.

What non-moving parts are excluded from this agreement? All parts and factory accessories, or items added to listed equipment and are required for proper operation, safety, and/or enhanced operational efficiency will be the responsibility of the vendor to maintain and repair or replace if needed. Any non-moving part that is deemed to not be needed by vendor and does not meet above conditions must be brought to the attention of Escambia County Facilities and valid reasoning must be presented in writing for wanted removal of part. Reasoning must include assurance that the removed part will not void any remaining factory warranties or in any way cause any unforeseen additional cost to Escambia County.

Does the county own the equipment for the water treatment (pumps/controller) or does it belong to the water treatment contractor? As far as I know the county does not own the pump/controllers that are installed at MC Blanchard.

What is the motor HP for the (3) condenser water pumps located in the cooling tower yard of the Judicial Center Energy Plant? These pump motors are 30hp 460/3ph.

Please provide clarification of EDDY Current Testing of the Centrifugal Chillers and not the Air-Cooled Chillers as mentioned during the site walk through? EDDY current testing will be done on all the applicable chillers.

The PM Scope of Work specify quarterly (4x) megging of motors & compressors but was mentioned during the site walk through that annual (1x) megging was sufficient and that condenser fan motors will not require megging. Can the County clarify this? Megging of the compressors, pump motors, and cooling tower fan motors will be done at least once a year. They do not have to be checked every quarter, but they all must be checked at least once during the year.

Can the County provide the Refrigerant Type and the total ILBS. of each of the York centrifugal chillers (Chiller #1, Chiller #2 and Chiller #4) located at the Judicial Center Energy Plant? They are as follows:

Chiller#1	840lbs	R-22

Chiller#2	2925lbs	 R-134a

Chiller#4	2150lbs	 R-134a

I forgot to mention but can you provide additional information on the Leonard Street Central Energy Plant and which of the chillers will require compressor (s) replacement; what chiller (s) and what compressor (s)?  It appears that on Chiller 1 compressor 2A is the one with issues, and on Chiller 3 compressor 2A is locked out.  This will need to be verified upon start of new contract with vendor.