RFB 21-03

Utilities Board of the City of Daphne

Digester Aeration/Mixing Modifications

Specifications

- GENERAL

  - SCOPE OF WORK

    - This section includes the design, manufacture, installation and start-up of a flexible membrane, fine pore aeration system including in-basin aeration components as shown on the Drawings and as specified herein.

    - The aeration system manufacturer shall provide single source responsibility for the complete fine bubble aeration systems including in-basin piping, diffuser assemblies and support components. Equipment must be installed by equipment manufacturer’s factory trained personnel.

  - DEFINITIONS

    - Tank:  Vertical walled reactor within which aeration occurs.

    - Diffuser Unit:  Fabricated unit including diffuser support frame and flexible membrane which releases air to the water.

    - Diffuser Assembly:  Fabricated assembly including disc holder, Clik lock wedge, flexible membrane, backer plate and retainer ring.

    - Air Drop Pipe:  Vertical piping section from out-of-basin header stub to in-basin aeration system.

    - Subheader Piping:  Air distribution piping from drop pipe to air laterals.

    - Air lateral Piping:  Air distribution piping from air manifold and diffuser assemblies.

    - Air Header Piping:  Out-of-basin air distribution piping from the blower building to the header stubs.

    - Blower Manifold Piping:  Air distribution piping between the blower discharge and air header piping.

    - Aeration Grid:  Associated piping and diffuser components connected to a single drop pipe.

    - Standard Cubic Feet per Minute (scfm):  Air at 68°F, 14.7 psia and 36% relative humidity.

    - Maximum Pressure:  Pressure in blower manifold piping at the specified airflow rate.

    - Oxygen Transfer Efficiency:  Percent of oxygen in the air stream that is dissolved to the wastewater under specified conditions of temperature, barometric pressure, airflow rate, and dissolved oxygen concentration.

    - Standard Oxygen Transfer Efficiency:  Percent of oxygen in the air stream that is dissolved to clean water under conditions of 68°F, 14.7 psia, and zero dissolved oxygen.

    - Air Distribution Uniformity:  Variation in air distribution between diffuser assemblies.

  - SYSTEM DESCRIPTION

    - Design Requirements:

      - Design in-basin air piping and diffusers to diffuse air throughout the aeration tank(s) in accordance with the specifications.

      - Design each diffuser assembly to provide uniform air release over the specified airflow range.

      - Design the aeration system to provide the minimum specified oxygen transfer efficiency at the specified airflow and operating pressure.

  - SUBMITTALS

    - General:

      - A detailed engineering submittal package shall be provided in sufficient detail and scope to confirm compliance with the requirements of this section.  Submittals shall be complete for all required components.  Partial submittals will not be accepted.

    - Shop Drawings:

      - Detailed layout drawings for in-basin aeration components.  Layout drawings shall include:

        - Layout and configuration of aeration system.

        - Detail drawings of diffuser assemblies showing components, method of construction, and attachment mechanism to air header distribution piping.

        - Detail drawings of all piping connections including drop to manifold, manifold to header and inline connections for manifold and headers.

        - Detail drawings of pipe support components.

    - Product Data:

      - Detailed listing of materials and materials of construction.

      - Product literature.

    - System Design and Performance Data:

      - Design calculations showing oxygen transfer based on guaranteed performance.

      - Include complete air headloss calculations for the aeration equipment from the top of the dropleg to the farthest diffuser bubble release point.

      - Design calculations showing uniformity of air distribution (+10% maximum variation) through lateral piping and diffuser orifice and diffuser media.

      - Design calculations for piping and support components.

      - Product Experience:

        - The supplier shall have experience in the design, manufacture, supply and commissioning of fine pore, flexible membrane aeration systems for a period of ten years.

        - If the Contractor elects to submit a substitute aeration system that does not comply with the above experience requirements, a bond guaranteeing the replacement of the aeration system shall be provided with the submittal package.

          - The bond term shall be for a period of five (5) years.  This term shall include the specified warranty period plus three (3) additional years.

          - If the operation of the aeration system as determined by the Owner is unsatisfactory, the Contractor shall repair, modify or replace the entire aeration system in a manner acceptable to the Owner.

          - Normal wear or malfunctions due to neglect or abuse shall not be considered justifiable reasons for unsatisfactory operations.

          - The presence of chemical compounds that are aggressive to the membrane material are not considered as normal wear or service.

          - If the Contractor fails to correct deficiencies identified by the Owner within six (6) months of the date first notified in writing, the Owner shall at it’s own discretion make all necessary repairs or replacement and deduct all associated costs from the Contractor’s bond.

      - Guarantee:

        - All equipment furnished under this contract shall be warranted to be free from defects in materials and workmanship for twelve (12) months from startup of the equipment or eighteen (18) months from shipment, whichever occurs first.  Defective part(s) shall be remedied by repair or replacement of the defective part(s) only shipped freight included, FOB original shipping point, by the Manufacturer.  Labor is excluded in this warranty.

Digester Equipment Demolition:

1.      Demolition and removal of all existing in-tank aeration equipment, after the    	     transition clamp at the bottom of the drop pipe, including piping, aeration       	    diffusers, supports and other ancillary components.

2.       Demolition and removal of the existing Invent Mixer located at the center of     	     the tank. Before removal, electrical connections to mixer will need to be 	   disconnected by others.

3.      Anchor bolts for pipe supports will be cut flush to the concrete floor.

    - Installation Instructions:

      - Installation requirements and guidelines for all proposed equipment shall be provided and approved prior to shipment.

      - Information on the aeration system shall include but not be limited to:

        - Diffuser unit assembly.

        - Diffuser assembly attachment.

        - Piping components and assembly.

        - Piping support components.

    - Operation and Maintenance Manuals:

      - Operation and Maintenance Manuals for all proposed equipment shall be provided and approved prior to shipment.

      - Information on the aeration system shall include but not be limited to:

        - Air flow balancing.

        - Diffuser assembly maintenance and membrane replacement.

        - Operational troubleshooting guidelines.

- PRODUCTS

  - MANUFACTURERS

    - Environmental Dynamics International, Columbia, Missouri.

    - Pre-approved equal.

      - Information on alternate manufacturers shall be submitted to the Design Engineer no less than 2 weeks prior to the bid date.  Only pre-approved, named manufacturers are acceptable.

  - MATERIALS

    - Welded Stainless Steel Components:

      - Sheets and plates of Type 304L stainless steel conforming to AISI 304L and ASTM A240.

      - Limit carbon content to 0.30% maximum.

    - Non-welded Stainless Steel Components:

      - Sheets and plates of Type 304 stainless steel conforming to AISI 304 and ASTM A240.

    - Fasteners and Anchorage Components:

      - 18-8 series stainless steel.

    - PVC Pipe and Fittings

      - Base material shall be ASTM D-1784.

      - Pipe shall be manufactured in accordance with ASTM D-1785 and ASTM D-2665.

  - AERATION EQUIPMENT

    - System Performance:

      - The aeration-mixing system shall be designed to meet the following:

        - Airflow = 	2563 scfm maximum

        - Maximum Airflow/Diffuser = 2.5 scfm/diffuser

        - Design Diffuser Submergence = 	16 feet maximum

    - Disc Diffuser Assembly:

      - The EDI FlexAir Integral Saddle Mount (ISM) Disc or Equal diffuser assembly shall be furnished and installed.

      - Each disc diffuser assembly shall include flexible membrane, retainer ring, disc holder with mounting saddle, Click lock wedge and o-ring seal.

      - Diffuser media shall have nominal dimensions of 9.0 inches in diameter with 59 square inches of perforated area.

      - The diffuser assembly with membrane media shall be fully supported over the full diameter with a 20% glass-filled polypropylene backer plate.

        - Use of a non-fully supported diffuser membrane is not acceptable.

      - The diffuser membrane shall be held in place by a threaded retainer ring.

      - The diffuser mounting connection shall allow installation of diffusers on PVC, CPVC, ABS, or metal lateral IPS sized piping of 3 inch or 4 inch diameter.

      - Diffuser mounting connection shall allow installation at the manufacturer’s facility or in the field.

      - Diffuser mounting connection shall allow for installation of additional diffusers, removal of diffusers, or change in location of diffusers without solvent welding in the field.

      - Mechanical Saddle attachment shall include air inlet port and positive locking mechanism to locate and lock the assembly to the air distributor piping.

      - Diffuser assemblies shall be shipped to the jobsite properly crated and protected for shipment and handling.

      - Diffuser saddle mount shall be 20% glass-filled polypropylene construction and shall be capable of withstanding an external force of 200 pounds without structural failure of the air distribution piping or diffuser assembly connection.

        - Small diameter threaded connections to attach diffusers to the air distribution header are not acceptable.

      - Saddle mount shall fully encompass the air distribution header and reinforce the pipe section at the diffuser assembly connection.

      - An O-ring gasket shall be provided to ensure an air tight seal between the mounting saddle and air header.

    - Flexible Membrane:

      - Membrane material for the diffuser unit shall be EPDM rubber.

        - Alternate membrane materials are not acceptable.

      - Membrane shall be molded in a single piece with the following characteristics.

        - Membrane shall be 9 inch inside diameter.

        - Perforated area on diffuser membrane shall be 0.41 square feet.

        - Non-perforated membrane section shall be provided to seal off air distribution orifices on the diffuser support structure.

      - The diffuser unit with membrane media shall be fully capable of operating under continuous or intermittent conditions and shall be designed with check valve capabilities to prevent entry of mixed liquor into the diffuser unit or air piping on air shutdown or interruption of air supply.  A minimum of three (3) integral check valve features shall be provided, not limited to the following:

        - Membrane shall be elastic and allow openings to close when the air supply is interrupted.

        - Membrane shall contract and shall seat on backer plate.

        - Membrane shall employ a non-perforated section that is aligned and seals against the air distribution orifices.

        - Use of independent or internal check valve components is not acceptable.

    - Aeration System Piping:

      - Out-of-basin air piping including blower manifold, air header, and header stubs are required and are to be supplied by the Contractor.

        - Header stubs shall extend to the inside top of the wall and terminate with a full diameter horizontal flange.

        - Out-of-basin piping may be unlined ductile iron, galvanized steel, stainless steel, or painted carbon steel.

        - The Contractor shall provide an isolating/balancing valve for control and distribution of air to the aeration grid and to allow isolating of the grid for inspection and maintenance on the header stub.

        - Isolation/balancing valve shall be positioned for accessibility from the top of the tank.

        - Each aeration grid shall have a moisture removal assembly (purge) located in the horizontal PVC piping at the base of the drop pipe. Purge shall consist of an ejector tube, removal hose and terminates at the top of the aeration tank with a manual valve. Purge line diameter will be ¾  inches.

      - Existing drop pipes shall be re-used.

        - Drop pipe shall connect to air manifold or subheader piping by means of a wrap-around clamp adapter constructed of 304 SS with elastomeric sleeve.

      - All submerged subheader distribution piping components shall be Schedule 40 PVC minimum.  All air lateral piping shall be SDR 26 minimum.

        - Use of PVC piping shall only be employed when the expected mean wall temperature is less than 140°C.  If temperature exceeds this limit, alternate materials shall be used or cooling loops added until the temperature is at the appropriate level.

        - Use of PVC piping shall only be employed when diffuser mounting system reinforces pipe wall at each mounting location.

        - Use of non-reinforced diffuser connections including threaded diffuser mounts is not acceptable.

        - Air piping sections shall have adjustable angle PVC positive locking flanges with stainless steel flange bolts

        - Systems employing soft couplings are not acceptable.

      - Pipe supports

        - Supports shall accommodate longitudinal movement in the piping components due to the thermal expansion and contraction over a temperature range of 100°F.

        - Supports shall be 304 stainless steel or glass filled polypropylene construction.

        - Fixed supports shall restrain the axial and rotational movement of the piping.

        - Simple supports shall allow unrestrained longitudinal movement of the in-basin piping.

        - All threaded connections shall be double-nutted.

        - Pipe straps shall be minimum 0.5 inch in width.

        - Supports shall allow leveling of the air piping with 2 inch minimum vertical adjustment at each support.

        - Pipe support spacing shall limit lateral deflection to 0.25 inch maximum.

        - Each pipe support shall be connected to basin floor by anchor bolts.

        - The integrated pipe support assembly shall be designed to withstand the associated uplift force of the piping and diffuser assemblies with a minimum design factor of safety equal to four (4).

        - Glass Filled Polypropylene (GFPP) supports shall incorporate the following features:

          - Klik-lock™ retainer strap to secure pipe to pipe support.

          - GFPP base to be mounted to floor with one anchor bolt.

          - Threaded base to allow bottom cradle of support to adjust in height.

          - Diameter of support base to be minimum 2.5inches (63mm) outer diameter.

    - Spare Parts:

      - Furnish the following spare parts and store as directed:

        - One percent of the total number of EPDM flexible membranes.

        - One set of special tools needed for installation or maintenance.

- EXECUTION

3.01	MANUFACTURING AND QUALITY CONTROL

A. The aeration system supplier shall submit documentation showing proof of operating an advanced manufacturing facility and in incorporating outstanding quality control programs.

B. Required documentation to satisfy 3.01.A for manufacturing shall be as a minimum.

- Manufacturing location and ownership by supplier.

- Percentage of outsourced manufacturing and assembly.

- Description of facility size and percentage under roof and outside.

- Overview of warehousing and ability to inventory key components.

- Listing of number of workers, type of jobs and experience level.

- Overview of in house tooling design and maintenance programs.

- Sample of work order and fabrication procedures.

- Description of staff training programs.

- Description of in house safety programs.

- Description of the plants degree of automation.

- Description of any scrap reduction, recycling or carbon reduction programs.

C. Required documentation to satisfy 3.01.1 for Quality Control shall be as a minimum.

- A complete description of in house Quality Control staff with title, duties and experience level.

- A complete description of in house process or material experts with title, duties and experience level who are key contributors to the manufacturing and QC processes.

- Sample quality control work Instruction plans for core products

- Sample product and process audit reports.

- Sample product performance testing reports.

- Outline of defined training programs for manufacturing personnel.

- Sample change control procedures.

- Sample quality plans for outside specialty vendors.

- List of compliance standards or accreditations.

- List of in house specialty test capabilities.

- Sample and description of product tracking capabilities.

3.02	SHIPPING AND SITE STORAGE

A. The aeration system supplier shall furnish a complete aeration system delivered to site in a clean and protected state. This includes all shipments from said supplier if items are dropped shipped to site from suppliers out sourced vendors. The cleanliness and protection of the aeration equipment shall be achieved as follows:

- Internal pipe surfaces shall arrive on site free of substantial dirt and debris and shall remain that way during on site storage thru the installation period. If installer during installation allows dirt and debris to enter and remain in pipe it is their responsibility to clean at the time of start-up. Keeping the internal surfaces of pipe clean requires supplier to.

  - Non-factory mounted diffuser holder installation ports shall be plugged for shipment and storage to prevent entry of water (rain or snow), dirt and debris.

  - Factory mounted diffuser holder airflow control orifices shall be plugged for shipment and storage to prevent entry of water (rain or snow), dirt and debris.

  - All flanged open ends, air distribution joints or flanged ends and manifold jointed or flanged open connection shall be capped and secured with a weather resistant cover to prevent entry of water (rain or snow), dirt and debris. The over shall be of a suitable size to cover and protect the flange or threaded surfaces of the joints.

  - All open pipe ends that are part of a fabricated system that will be attached by solvent welding, metal to metal welding or coupled with a mechanical coupling shall be capped with a suitable weather tight cap to nit only prevent entry of water, dirt and debris but to protect the surface of the pipe.

  - Factory mounted diffuser holders shall be packed to prevent the collection of and stagnation of water and promotion of algae growth.

  - All pipe shall be put on pallets and secured in place by proper framing designed to be

    - Lifted by forklift or crane off flatbed trucks.

    - Removed easily from export containers.

- Diffusers and diffuser assemblies shall be boxed to prevent damage to membrane surfaces and holders. The boxes should then be placed on a pallet and the whole pallet wrapped with a UV resistant shrink wrap material. Material should be capable of:

  - Long term outdoor storage if indoor storage is not available.

  - Stand up to and remain intact if transported on an open top carrier.

  - Have the strength to hold the shape of the palletized material.

- Ancillary equipment such as supports, anchors, hardware, miscellaneous plastic parts, hoses etc. shall be boxed and labeled as required and placed in shipping crates. The shipping crate should then be shrink wrapped with a UV resistant material as described in section 3.01.A.2

B. Shipping to site

- The aeration supplier shall take all necessary precautions in making sure the aeration equipment is shipped to site minimizing any damage. Precaution actions include:

  - Loading the truck in such a manner to avoid over stacking of material and damage to lower stacks.

  - Strapping to solid skid framing and not on pipe material.

  - Packing for ease of removal on site either from open flatbed, closed van or export container.

  - Dedicated load shipping and no repacking to another carrier. Multiple site shipments on same truck are allowed to save space and transport costs.

- The aeration supplier shall do everything possible to marshal equipment from sub vendors and combine to avoid multiple shipments of small loads to site.

C. Site Storage

- The site owner is required to provide a suitable flat laydown space for the aeration system pipe works.

- The preferred storage for the diffusers and boxed items would be inside or undercover.

  - INSTALLATION

    - Equipment must be installed by equipment manufacturer’s factory trained personnel.

    - Diffuser assemblies on a common grid shall be installed within an elevation tolerance of ±1/2 inches.

    - Air piping including blower manifold, header, and in-basin piping must be clean prior to delivering air up the diffusers.

    - Installer shall be responsible for cleanliness of piping and may be required to manually clean pipe, or air or water flush piping as required.

  - START-UP

    - After installation is completed, the installer shall perform the following field tests in the presence of the Engineer and the Owner.

      - Fill the reactor to the bottom of the diffuser assemblies.

      - Adjust the pipe supports and diffuser assemblies such that all diffuser units are installed within ±1/2 inches of the design diffuser elevation.

      - Fill the reactor to a level of 2 feet above the top of the diffusers.

      - Release air to the system and inspect the system for air leaks at all piping or diffuser connections.

      - Check all membrane for cuts or tears that may have occurred during the installation.

      - Adjust any piping or diffusers that show leaks or disproportionate amount of airflow.

      - Operate the blowers at the design air rate and observe air release and air distribution patterns.

      - All water, air, power and labor associated with testing and adjustment of diffuser assemblies are to be supplied by Owner.

    - MANUFACTURER’S FIELD SERVICES

      - A manufacturer’s personnel shall be present at the job site to inspect the installation of the equipment, start-up the system, and train operations and maintenance personnel on the supplied equipment.