Ridgewood East Phase 1 - Part 1 Water Main Replacement Project and

Part 2 (22nd/24th Street NE) Roadway Reconstruction Project

Addendum 1
City of Canton, Ohio

Purchasing Department

218 Cleveland Ave. SW, 6th floor

Canton, Ohio 44702

Ridgewood East Phase 1 - Part 1 Water Main Replacement Project and

Part 2 (22nd/24th Street NE) Roadway Reconstruction Project
Item/Project

Water Department

Responsible Department

Thursday, March 29, 2018 at 2:00 PM local time

Bids Due On or Before

Bid Proposal Submitted By:

Company Name 

Street Address

City

           





State



     Zip

Contact Person

           
     Phone No.



          Email Address

Invitation to Bid Change 1:
A.
In Appendix E: Technical Specifications and Drawings, plan sheet 17; the “Typical Water Service” detail shall be replaced with the attached detail.
Addendum 1[image: image1.jpg]R/W

ROADWAY BOX, HEAVY
DUTY, R144 COMPLETE

(SEE NOTE 4 BELOW)

CURB SIDEWALK
ROADWAY |
3'—6" MINIMUM
5'—0" MAXIMUM
VARIABLE 4+ 6'+ *

HDPE TUBING, CTS‘\

PE4710

\PIPING FROM CURB VALVE TO
BUILDING AND CONNECTION TO
CURB VALVE BY OTHERS.

CURB VALVE,
DISTRIBUTION MAIN MUELLER MARK Il ORISEAL (H-15172)
LOCATION VARIES (POINT OF DELIVERY TO CUSTOMER)

CORPORATION STOP
(SEE NOTE 1 BELOW)

NOTES:
1.) CORPORATION STOP AND ASSEMBLY SHALL BE AS FOLLOWS:
1”7 CORP. STOP ON DIP: INSTALL AT A 45" ANGLE, A MUELLER H—15000 CORPORATION STOP WITH
A McDONALD 74750Q ELBOW.
1”7 CORP. STOP ON PVC C809: |INSTALL AT A 45" ANGLE, A MUELLER H—15000 CORPORATION
STOP WITH A McDONALD 74750Q ELBOW AND A FORD, STAINLESS
STEEL, EPOXY COATED TAPPING SADDLE (FC202 STYLE).
1 %" CORP. STOP: INSTALL AT A 45" ANGLE, A MUELLER H—15000 CORPORATION STOP WITH
MUELLER H-15083 ELBOW AND A MUELLER H-15071 COMPRESSION FEMALE
WITH INSERT COUPLING. ASSEMBLY SHALL ALSO CONSIST OF A FORD,
STAINLESS STEEL, EPOXY COATED TAPPING SADDLE (FC202 STYLE).
2" CORP. STOP: INSTALL AT A 45" ANGLE, A MUELLER H—10003 CORPORATION STOP WITH 2" IRON
TOF, A STANDARD NO LEAD BRASS 45 ELBOW AND A MUELLER H—-15428
COMPRESSION MALE WITH INSERT COUPLING. ASSEMBLY SHALL ALSO CONSIST OF
A FORD, STAINLESS STEEL, EPOXY COATED TAPPING SADDLE (FC202 STYLE).

2.) NO SWIVEL ELBOWS WILL BE PERMITTED.
3.) A SERVICE CLAMP MUST BE USED WHEN THE MAIN SIZE IS 2 INCH OR SMALLER.

4.) HEAVY DUTY VALVE BOXES, COMPLETE, MUST BE USED IN PLACE OF ROADWAY BOXES WHEN
LOCATED IN ROADWAYS OR ASPHALT DRIVES.

5.) APPROVED EQUALS MAY BE USED IN PLACE OF SPECIFIED ITEMS.

TYPICAL WATER SERVICE
(C94)





Page 2 of 3

