| Lisa Lane, Purchasing Agent 200 N Castle Hgts Ave Lebanon, TN 37087 Phone: 615-443-2802 Fax: 615-443-2849 lisa@lebanontn.org |  |
| --- | --- |

CONTRACT SPECIFICATIONS FOR:

Heater and Air Conditioner Replacements for the Water Treatment Plant

REQUEST FOR PROPOSALS:  RFP #0223-HVAC2023

CONTACT:	City of Lebanon Purchasing Office

Lisa Lane, Purchasing Agent

200 N Castle Heights Ave

Lebanon, TN  37087

(615) 443-2802

DATE ISSUED: February 1st , 2023

DUE DATE: February 23rd , 2023, 2:00 PM

Please note:  If documents were downloaded from the City of Lebanon website, bidder is responsible for obtaining any addenda either through updates on the website or by contacting he Purchasing Agent listed above.

CITY OF LEBANON, TENNESSEE

DETAILED SPECIFICATIONS FOR

Heaters and Air Conditioner Replacements for the Water Treatment Plant

RFP #0223-HVAC2023

_______________________________________________________________________________________

*City of Lebanon reserves the right to reject all or any part of any RFP*

The City of Lebanon is exempt from State Tax and Federal Exercise Tax.

NO PROPOSALS RECEIVED AFTER CLOSING WILL BE ACCEPTED.

The City of Lebanon invites sealed proposals for HVAC replacement units, in accordance with the specifications and bidding instructions set forth in this Request for Proposal. Proposals will be received by the Purchasing Department, 200 N. Castle Heights Avenue, Lebanon, Tennessee 37087, until 2:00 p.m. local time, February 23rd , 2023, at which time they will be opened and read aloud.

Please identify as a sealed proposal with the following information on the envelope:

“RFP #0223-HVAC2023”.

Any questions regarding this proposal should be directed to Lisa Lane, Purchasing Agent, (615) 443-2802.

A copy of the bid tabulation will be available upon written request to the Purchasing Department.

Any manufacturers’ names, trade names, brand names, or catalog numbers used in the specifications are for the purpose of describing and establishing general quality levels.  Such references are not intended to be restrictive.  Since the “City” does not wish to rule out other competition and equal brands or makes and models, please remember, “Any Approved Equal”.  However, if a service other than specified in the bid, it is the vendors responsibility to prove to the City of Lebanon that said service is equal to or exceeds the quality of the specifications listed for services provided.

The City of Lebanon is an equal opportunity entity and does not discriminate based on age, race, sex, national origin, religion, or disability in admission to, access to, or operations of its programs, services, activities, or in its awarding of such bids in Pursuant to Title VI of the Civil Rights Act of 1964.  All vendors must be incompliance with all City Codes and current with all City fees and taxes to be considered as a responsive bidder or participant in this process.

SCOPE

The purpose of this proposal is to provide information for heater and air conditioner replacements at the City of Lebanon Water Treatment Plant, including an explanation of the work and job requirements, that meet the specifications listed in this proposal.  The work covered in these specifications consists of installation, labor, equipment, removal and disposal of existing units, and materials to perform all operations that will provide complete installation.  Special care must be taken to protect sensitive areas underneath the heater locations during demolition and installation.

CLASSIFICATION

The heater and air conditioner replacements in this Request for Proposal, herein after referred to as RFP, shall be of the following types either “equal to “or “better than”.

LOCATION

City of Lebanon Water Plant

7 Gilmore Hill Road

Lebanon, Tennessee 37087

SPECIFICATIONS FOR HEATERS

Replacement of (6) Solaronics Suntube IV infrared tube heaters with (6) low profile hanging forced air propane heaters.  Bid must include removal and disposal of existing heaters, installation and venting of new heaters with new thermostats.

New heaters shall be Dayton, low profile, 120,000 BTU, Part #2RYV4A or similar with the following:

- Low-profile unit heater product type

- Natural gas/propane fuel

- Field convertible combustion type

- Heating Capacity Input & Output:  120,000 BTUH Input; 98,400 BTUH Output

- Propeller fan type

- 82 % thermal efficiency rating

- 4 in flue diameter

- Overall Height, Width, Depth:  22-5/8 in H x 30 in W x 26-3/8 in

- Air Flow & Direction:  1,475 cfm (flow); Horizontal (direction)

- 60˚ F air temperature rise

- 5 in burner size inlet size

- Direct drive type

- Fan Diameter & Frequency:  16 in (diameter); 60 hz (frequency)

- Gas Connection Size & Type:  ½ in (size); NPT, Male (type)

- Heat Exchanger Gauge & Material:  20 ga (gauge); aluminized steel (material)

- Heat Output, Voltage, Method:  98,400 BTUH (output); 115V AC (voltage); fan forced (method)

- Direct spark ignition type

- Indoor Air Discharge Height, Width:  22-5/8 in H x 30 in W

- 6.4A maximum amperage

- Motor Speed & Type:  1,050 RPM (speed); SP (type)

- Mounting Height, Hole Diameter and Mounting Location:  8ft to 12ft (height); 3/4in (diameter); ceiling (location)

- Phase 1

- Profile Type & Vent Type:  Low profile type, Power vent type

- Thermostat must be included

Features:

Power venting allows horizontal venting through side walls or vertical venting, tubular heat exchanger and single burner design with gas conversion kit included.

- Includes LP gas conversion kit.

- 10 year manufacturer’s warranty length on heat exchanger, burners and flue collectors – all other parts are 1 year warranty.

- ETL; ETLc Certified Standards

- UNSPSC – 40101806

- Country of Origin:  USA (subject to change)

Replacement of (4) 10KW Qmark electric 480v/3ph heaters; shall include heater, installation, hanging, disposal, any electrical work required and thermostat controls installed.

New heaters shall be Dayton 2YU70 480v/3ph heaters of similar with the following:

- Overall Height, Width, Depth:  21-3/4 in H x 19 in W x 8-1/2 in D

- 480V AC Voltage

- Air Flow & Temperature Rise:  650 cfm (flow); 49˚ F (temperature rise)

- Phase 3

- Heating Method and Capacity:  Fan forced (method); 34,100 BTUH (capacity)

- 18 ft horizontal air flow

- Frequency & Amperage:  60 hz (frequency); 12A (amperage)

- Mechanical selector dial control type

- 24V AC Contactor Coil Voltage

- Housing Color, Finish, & Material:  beige (color); powder coated (finish); steel (material)

- Vertical Floor Coverage & Mounting H:  26 ft (coverage); 14 ft (mounting)

- Requirement:  2YU95; 5/16”-18 threaded rod for ceiling installation

Features:

- Includes adjustable air outlet louvers

- 1 year warranty for parts, 5 year warranty for elements

- UL Listed CUL Standards

- 10kW wattage output

- UNSPSC – 40101819

- Country of Origin:  USA (subject to change)

SPECIFICATIONS FOR AIR CONDITIONERS

Replacement of (2) 36,000 BTU portable air conditioners and (2) 13,000 BTU portable air conditioners.  Bid must include the removal and disposal of existing air conditioners, installation of new air conditioners and ductwork.

New air conditioning units shall be (2) MovinCool Climate Pro K36 and (2) MovinCool Climate Pro X14 or similar with the following:

Pro X14:

- Heavy duty rating

- HVAC operation mode, cooling only

- 13,200 BTUH cooling capacity

- EER, Amps, Watts, Voltage, Hz:  10 (EER); 11 A (amps); 1,300 W (watts); 115V AC (voltage); 60 hz

- Phase 1

- HVAC NEMA plug configuration – LCDI, 5-15P

- 10 ft power cord length

- Air cooled vented system cooling method

- Electronic control type

- Capable of weekly programmable schedules

- Remote control functions:  No remote control

- No smart connectivity

- 60 dBA sound level

- 3 speeds

- 440/410/385 supply air flow

- 30 ft maximum supply hose length

- 830/770/720 exhaust air flow

- 60 ft maximum exhaust hose length

- 5 gal condensate tank capacity

- 70˚ to 113˚ F ambient operating range

- Height, Weight, Depth:  48 in H x 22 in W x 29 in D

Features:

- Includes (2) cold air nozzles

- UL 60335-1; UL 60335-2-43 Standards

- Adjustable cool air discharge nozzles

- UNSPSC – 26111704

- Country of Origin:  Japan (subject to change)

Pro K36:

- Heavy duty rating

- HVAC operation mode, cooling only

- 36,000 BTUH cooling capacity

- EER, Amps, Watts, Voltage, Hz:  8 (EER); 19.6 A (amps); 4,300 W (watts); 208/230V AC (voltage); 60 hz

- Phase 1

- HVAC NEMA plug configuration – LCDI, 6-30P

- 6 ft power cord length

- Air cooled vented system cooling method

- Electronic control type

- Capable of weekly programmable schedules

- Remote control functions:  No remote control

- No smart connectivity

- 70 dBA sound level

- 3 speeds

- 920/880/840 supply air flow

- 40 ft maximum supply hose length

- 1390/990 exhaust air flow

- 60 ft maximum exhaust hose length

- 5 gal condensate tank capacity

- 65˚ to 95˚ F ambient operating range

- Height, Weight, Depth:  53 in H x 31 in W x 55 in D

Features:

- UL 60335-1; UL 60335-2-45 Standards

- Louvers cool air discharge

- UNSPSC – 40101806

- Country of Origin:  Japan (subject to change)

PROPOSAL SUBMISSION

To be considered, Proposers must submit a complete response to this RFP.  Proposals must be signed by an official authorized to bind the Proposer to its provisions.  Proposals must include a statement as to the period during which the proposal remains valid but for purposes of this RFP, the period must be at least ninety (90) days.

Two (2) copies of the proposal package shall be enclosed in a sealed envelope plainly identified in the upper left-hand corner with the company’s name and address and in the lower left-hand corner.

The City reserves the right to reject, any and all proposals and to waive information, irregularities, and technicalities in the process.  The City may negotiate separately with any source in any manner necessary to arrive at a contract agreement that is in the best interest of the city.

Proposals may be hand-delivered or mailed to the above address by the date and time specified.  It is the responsibility of the Proposer to deliver the RFP.  Proposals dispatched, but not received by the City Purchasing Department by proposal closing time, will be returned, after receipt, unopened to the prospective Proposer.  Verbal or emailed quotes will not be accepted at any time.

COST CERTIFICATION

The undersigned hereby certifies that I have read all items of the RFP and fully understand the requirements listed herein.  I further certify that I am an authorized agent of the offering firm and may be held liable for any or all remedies that may become due to the City of Lebanon.

NOTICE TO PROPOSERS

To be considered, prospective consultants are required to submit all requested information including pricing detail.  Pricing should include all costs related to the cost of the equipment, installation, hardware, labor, materials, removal, and disposal, etc., for HVAC replacement units.

The total project cost is a major factor in the decision process, but not the only consideration.  Other decision factors are the consultant’s identification and understanding of the City’s requirements.

Questions and Additional Information:

For clarification or additional information, contact the Purchasing Department (615) 443-2802 or via email to lisa@lebanontn.org.  You may also contact J.C. York, Plant Manager (615) 444-0485.

GENERAL CONDITIONS

Hold Harmless

Consultant shall protect, indemnify, and hold the City harmless from and against any damage, cost, or liability for any injuries to person or property arising from acts or omissions of the consultant, his employees, agents, or sub-contractors, howsoever caused.  The successful proposer agrees that they will function as an independent contractor and agrees to indemnify and hold harmless the City of Lebanon, its Council Members, employees, officers, and agents from, any and all claims or demands that may arise out of or relate to its duties contracted for pursuant to goods and/or service.

Response Preparation Costs

The City will not pay any costs incurred by any vendor in the proposal preparation, printing, demonstration, or negotiations process.  All costs shall be the responsibility of the proposing consultants.

Acceptance of Proposal Content

Proposals to be valid for a minimum period of ninety (90) days from date of receipt by the City.

Addenda

Any change to this RFP will be brought forward in the form of a written addendum from the Purchasing Department and will be provided to all known interested parties.  No oral interpretations or communication will affect or change in any way the information contained herein.

Rights and Options of the City of Lebanon:

The City reserves the following rights and options:

- Determine those proposers who are most qualified

- Reject any or all proposals for any reason, at its sole discretion.

Proposal Evaluation

City of Lebanon’s staff will review the proposals submitted and make a recommendation to the City Council.  It is expected that the selected vendor will begin work shortly after an agreement is executed.  The final deliverables will be due on a mutually agreed upon schedule.  The basis for the evaluation of proposals received includes, but is not limited to, cost, delivery, capability of company, etc.

Contract Award

The contract award, if made, shall be to the lowest, best, and most responsive proposal that, is considered to be the City’s best interest.  Anticipated award will be after recommendation approval by the Lebanon City Council.

PRICING SHEET

Removal and disposal, venting, install new thermostats and units, any electrical work required, labor, equipment, and all materials needed to complete the installation of the HVAC replacement units at the City of Lebanon Water Treatment Plant.

Total cost for completion of work $_____________________________

Total Bid $____________________________

______________________________________________________________________

Company Name and Authorized Representative

______________________________________________________________________

Address, Contact Phone Number

__________________________________________

Email Address

GUARANTEE:

In the event the awarded vendor does not perform any or all parts of the agreement to the satisfaction of the City of Lebanon, the vendor will be given a 30-day written notice of cancelation.

SIGNATURE PAGE

Signature for Contract with:  ________________________________________________________

HVAC Replacement/ Installation Company or Contractor

Recommend:					Contractor:

____________________________________             _____________________________________

Commissioner of Finance

Title _________________________________

Approved as to Form & Legality:

____________________________________

City Attorney

Sworn to & subscribed to before being a Notary Public, this day of ____________________,

2023.  By ______________________________, of Contractor and duly authorized to execute

this instrument on the Contractors behalf.

_________________________________________

Notary Public

_________________________________________

My Commission Expires

Executed By:

_________________________________________

Mayor, City of Lebanon