SPECIFICATIONS FOR INSTALLATION OF DEHUMIDIFICATION AND AIRCONDITIONING SYSTEM FOR THE NATATORIUM AT THE MANCHESTER RECREATION COMPLEX

Requested bidders, please provide a “TURNKEY PRICE” for the DEMOLISHING and REPLACEMENT of the existing indoor pool HVAC equipment including the following:

- ALL BIDDERS ARE REQUIRED TO DO A SITE EVALUATION AT 557 NORTH WOODLAND STREET AND MEET WITH THE OWNER PRIOR TO SUBMITTING A BID.

- T.C.A. 12-4-201 requires a payment bond of 25% of the contract price.  In addition, T.C.A. 12--     207 requires a bond to pay taxes and licenses.

3.    BIDS ARE DUE ON THURSDAY, SEPTEMBER 8 AT 10:00AM.  THEY MUST BE SEALED WITH CONTRACTORS NAME, LICENSE NUMBER ON THE OUTSIDE.  IF MAILED OR DELIVERED THEY MUST BE RECEIVED BEFORE THE BID DEADLINE.  THEY CAN BE MAILED OR DELIVERED TO BRIDGET ANDERSON, FINANCE DIRECTOR CITY OF MANCHESTER, 200 WEST FORT STREET MANCHESTER TENNESSEE.  ALL QUESTIONS REGARDING THE BID MAY BE ADDRESSED TO BONNIE GAMBLE, DIRECTOR PARKS AND RECREATION, BGAMBLE@CITYOFMANCHESTERTN.COM OR 931-728-0273

4. Owner reserves right to accept or reject any or all Bids, reject a Bid not accompanied by a required      Bid Security or by other data required by Bidding Documents, reject a Bid which is in any way incomplete, illegible, unsigned, improperly signed or sealed, obscure, or reject a Bid which contains arithmetical errors, erasures, alterations, or irregularities of any kind.

Bids received after scheduled opening time will be returned to Bidder unopened.

5.  Bidders must submit a reference list of a minimum of five commercial HVAC dehumidification installs for commercial indoor pools and that they have been in the HVAC commercial installation business for at least 10 years.

BASE BID

- DEMOLISH existing Dectron indoor pool unit included indoor AHU and outdoor air cooled condenser.

- DEMOLISH existing AAON

- Installation Contractor are to provide design drawings as necessary for a COMPLETE FUNCTIONING SYSTEM. ANY DRAWINGS MUST SHOW COMPLETE COORDINATION WITH PLANS OF MANUFACTURER.

- REPLACE THE DECTRON UNIT AS FOLLOWS:

  - Equipment Vendor to provide two (2) OUTDOOR PACKAGED RTUs designed for indoor pool/applications and configured per below specs capable of maintaining indoor space temperature and humidity set points per facility requirements.  Design ambient conditions are 95/78 summer and 10/9 winter. The total of the two (2) units performance is as follows: Total Cooling / Dehumidification Tons = 130 tons, lb./hr. moisture removal total = 580 lbs./hr. **Do not replace with like for like capacity as the existing system was utilizing an energy recovery wheel to reduce the mechanical cooling requirement. That heat recovery has been eliminated due to the corrosive environment and service and maintenance aspects as well as the lack of significant payback in this application. Due to this deletion additional mechanical cooling is required to meet the space load.

  - The Vendor shall include a 2 year parts and 1 year labor warranty on the entire unit, 5 year coil coating warranty per below spec, 5 year compressor parts warranty. The Vendor shall provide full startup services as well as a 2 year preventative maintenance contract, 8 hours of owner instruction at the owner’s request which could be broken into multiple occasions, BACNET BMS interface, and remote monitoring capability using Wi-Fi and web user interface software. Vendor shall include 1st year remote monitoring in the labor warranty. Local vendor shall provide local training opportunities within the first year of warranty for detailed unit control and operation intensive class. Provide plenum curbs with side SA/RA duct connections including service platforms on 3-sides of unit for ease of service access. Provide unit mounted user interface with Touch Screen and full graphics package with unit monitoring, alarms, control set point manipulation, trend logging, unit IOM, and unit parts list accessible on the unit control interface. Provided units must meet or exceed the below Indoor Pool A/C/Dehumidification/ Heating Rooftop Unit specification sheets and include above additional listed items.

  - Vendor to provide standard lead times with quote as well as a premium adder for expedited lead times to meet a 5-6 week delivery.

  - Installer to provide labor, materials and performance bond to demolish existing Dectron and AAON units; install new units including the addition of below NG Pool Water Heater and associated recirculating pump; upgraded electrical service sized for new equipment, new controls wiring including remote mtd sensors as well as BMS interface wiring and programming installed at owner’s computer also installer to extend/replace ductwork for SA/RA from building existing duct/louvers to the two new units plenum curbs including insulation for outdoor application; installer to extend hot water heating piping to new units including installation of hot water control valves, piping packages, and associated control/power wiring and electric heat trace the hot water piping; installer shall extend outdoor concrete pads or otherwise provide structural support for the new equipment. Installer shall also provide T&B services to set up min OA, SA CFM, RA CFM for both units as well as set flow rates for Pool Heater and hot water heating coils. Installer to provide site cleanup, touch up of surfaces, disposal of all trash and debris as well as disposal of demolished equipment and ductwork/piping/electrical. Installer to move/extend existing fire/smoke alarms to new equipment.

  - Add an outdoor natural gas “Finned Water-Tube Pool Heater with 842mbh output minimum to handle the pool heating for the therapy pool including the Cold Water Run accessory. Extend existing natural gas piping to the new outdoor boiler and provide all code required gas piping required accessories including but not limited to gas regulator to match new boiler. Provide/extend existing pool water heating piping out to the new outdoor boiler using CPVC high temp rated or other high temp rated piping materials for water temperatures up to 160 deg F. Water heater must meet the below “Finned Water-Tube Pool Heater Specificiations”. Provide hot water shut off valves, P-T fittings, t’stat control wiring, Flue/Combustion venting materials, gas piping, electrical wiring, concrete slab, anchorage to meet the manufacturers IOM and all Code requirements. Include pool water heating recirculating pump, motor starter, installation, electrical wiring, piping, and control wiring.

Guide Specifications – Indoor Pool A/C/Dehumidification/Heating Rooftop Unit

Part 1 - General

1.01 Related Documents

1.02 General Description

- This section includes the design, controls and installation requirements for packaged rooftop units / outdoor air handling units.

1.03 Quality Assurance

- Packaged air-cooled condenser units shall be certified in accordance with ANSI/AHRI Standard 340/360 performance rating of commercial and industrial unitary air-conditioning and heat pump equipment.

- Unit shall be certified in accordance with UL Standard 1995/CSA C22.2 No. 236, Safety Standard for Heating and Cooling Equipment.

- Unit and refrigeration system shall comply with ASHRAE 15, Safety Standard for Mechanical Refrigeration.

- Unit Energy Efficiency Ratio (EER) shall be equal to or greater that prescribed by ASHRAE 90.1, Energy Efficient Design of New Buildings except Low-Rise Residential Buildings.

- Unit shall be safety certified by ETL and ETL US listed.  Unit nameplate shall include the ETL/ETL Canada label.

- Unit shall be approved for use in and outside High Velocity Hurricane Zones (HVHZ) by the Florida Building Code (FL# 15031), when using the required steel rooftop curb and attachment methods.Maximum allowable lateral wind pressure is +100psf/-100psf. Maximum allowable uplift is +50psf/-50psf. Positive and negative required design pressures calculated for use with this system shall be determined by others on a job specific basis, in accordance with the governing code. Site specific pressures shall be less than or equal to the listed positive or negative allowable lateral wind design pressure and allowable uplift values for the product.

1.04 Submittals

- Product Data: Literature shall be provided that indicates dimensions, operating and shipping weights, capacities, ratings, fan performance, filter information, factory supplied accessories, electrical characteristics and connection requirements. Installation, Operation, and Maintenance manual with startup requirements shall be provided.

- Shop Drawings: Unit drawings shall be provided that indicate assembly, unit dimensions, construction details, clearances and connection details. Computer generated fan curves for each fan shall be submitted with specific design operation point noted. Wiring diagram shall be provided with details for both power and control systems and differentiate between factory installed and field installed wiring.

1.05 Delivery, Storage, and Handling

- Unit shall be shipped with doors screwed shut and outside air hood closed to prevent damage during transport and thereafter while in storage awaiting installation.

- Follow Installation, Operation, and Maintenance manual instructions for rigging, moving, and unloading the unit at its final location.

- Unit shall be stored in a clean, dry place protected from construction traffic in accordance with the Installation, Operation, and Maintenance manual.

1.06 Warranty

- Manufacturer shall provide a limited “parts only” warranty for a period of 12 months from the date of equipment startup or 18 months from the date of original equipment shipment from the factory, whichever is less. Warranty shall cover material and workmanship that prove defective, within the specified warranty period, provided manufacturer’s written instructions for Installation, Operation, and maintenance have been followed. Warranty excludes parts associated with routine maintenance, such as belts and filters.

Part 2 - Products

2.01 Manufacturer

- Products shall be provided by the following manufacturers:

- Manufactures that make equipment specifically for Indoor Pool A/C/ Dehumidification/ Heating application for 10 years or more and meet or exceed this entire specification.

2.02 Rooftop Units

- General Description

- Packaged rooftop unit shall include compressors, evaporator coils, filters, supply fans, dampers, air-cooled condenser coils, condenser fans, reheat coil, hot water coils, return fans, and unit controls.

- Unit shall be factory assembled and tested including leak testing of the DX coils, leak testing of the hot water coils, pressure testing of the refrigeration circuit, and run testing of the completed unit. Run test report shall be supplied with the unit in the service compartment’s literature pocket.

- Unit shall have decals and tags to indicate lifting and rigging, service areas and caution areas for safety and to assist service personnel.

- Unit components shall be labeled, including pipe stub outs, refrigeration system components and electrical and controls components.

- Estimated sound power levels (dB) shall be shown on the unit ratings sheet.

- Installation, Operation, and Maintenance manual shall be supplied within the unit.

- Laminated color-coded wiring diagram shall match factory installed wiring and shall be affixed to the interior of the control compartment’s hinged access door.

- Unit nameplate shall be provided in two locations on the unit, affixed to the exterior of the unit and affixed to the interior of the control compartment’s hinged access door.

- Construction

- All cabinet walls, access doors, and roof shall be fabricated of double wall, impact resistant, rigid polyurethane foam panels.

- Unit insulation shall have a minimum thermal resistance R-value of 13. Foam insulation shall have a minimum density of 2 pounds/cubic foot and shall be tested in accordance with ASTM D1929-11 for a minimum flash ignition temperature of 610°F.

- Unit construction shall be double wall with G90 galvanized steel on both sides and a thermal break. Double wall construction with a thermal break prevents moisture accumulation on the insulation, provides a cleanable interior, prevents heat transfer through the panel, and prevents exterior condensation on the panel.

- Unit shall be designed to reduce air leakage and infiltration through the cabinet. Cabinet leakage shall not exceed 1% of total airflow when tested at 3 times the minimum external static pressure provided in AHRIStandard 340/360. Panel deflection shall not exceed L/240 ratio at 125% of design static pressure, at a maximum 8 inches of positive or negative static pressure, to reduce air leakage. Deflection shall be measured at the midpoint of the panel height and width. Continuous sealing shall be included between panels and between access doors and openings to reduce air leakage. Piping and electrical conduit through cabinet panels shall include sealing to reduce air leakage.

- Roof of the air tunnel shall be sloped to provide complete drainage. Cabinet shall have rain break overhangs above access doors.

- Access to filters, dampers, cooling coils, reheat coil, return fans,compressors,and electrical and controls components shall be through hinged access doors with quarter turn, zinc cast, lockable handles. Full length stainless steel piano hinges shall be included on the doors.

- Exterior paint finish shall be capable of withstanding at least 2,500 hours, with no visible corrosive effects, when tested in a salt spray and fog atmosphere in accordance with ASTM B 117-95 test procedure.

- Units with cooling coils shall include double sloped 304 stainless steel drain pans.

- Unit shall be provided with base discharge and return air openings. All openings through the base pan of the unit shall have upturned flanges of at least 1/2 inch in height around the opening.

- Unit shall include lifting lugs on the top of the unit.

- Unit shall include interior corrosion protection which shall be capable of withstanding at least 2,500 hours, with no visible corrosive effects, when tested in a salt spray and fog atmosphere in accordance with ASTM B 117-95 test procedure. Air tunnel, fans and dampers shall all include the corrosion protection.

- Unit base shall be fabricated of 1 inch thick double wall, impact resistant, rigid polyurethane foam panels.

- Unit shall include factory wired control panel compartment LED service lights.

- Electrical

- Unit shall be provided with factory installed and factory wired, non-fused disconnect switch.

- Unit shall be provided with a factory installed and factory wired 115V, 13 amp GFI outlet disconnect switch in the unit control panel.

- Unit shall be provided with phase and brown out protection which shuts down all motors in the unit if the electrical phases are more than 10% out of balance on voltage, the voltage is more than 10% under design voltage or on phase reversal.

- Unit shall be provided with blower auxiliary contacts on the low voltage terminal block which close when the supply fans are energized.

- Unit shall be provided with remote stop/start terminals which require contact closure for unit operation. When these contacts are open the low voltage circuit is broken and the unit will not operate.

- Supply Fans

- Unit shall include direct drive, unhoused, backward curved, plenum supply fans.

- Blowers and motors shall be dynamically balance and mounted on rubber isolators.

- Motors shall be premium efficiency ODP with ball bearings rated for 200,000 hours service with external lubrication points.

- Variable frequency drives shall be factory wired and mounted in the unit. Fan motors shall be premium efficiency.

- Return Fans

- Unit shall include direct drive, axial flow return fans. Blades shall be adjustable pitch.

- Unit shall include barometric relief dampers.

- Fans and motors shall be dynamically balanced.

- Motors shall be premium efficiency ODP with ball bearings rated for 200,000 hours service with external lubrication points.

- Access to return fans shall be through double wall, hinged access doors with quarter turn lockable handles.

- Variable frequency drives shall be factory wired and mounted in the unit. Fan motors shall be premium efficiency.

- Cooling Coils

- Evaporator Coils

- Coils shall be designed for use with R-410A refrigerant and constructed of copper tubes with aluminum fins mechanically bonded to the tubes and galvanized steel end casings. Fin design shall be sine wave rippled.

- Coils shall have interlaced circuitry and shall be 6 row high capacity.

- Coils shall be hydrogen or helium leak tested.

- Coils shall be furnished with factory installed expansion valves.

- Coils shall have a flexible, epoxy polymer e-coat uniformly applied to all coil surface areas without material bridging between fins. Humidity and water immersion resistance shall be up to a minimum 1,000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92). Corrosion durability shall be confirmed through testing to no less than 6,000 hours salt spray per ASTM B117-90. Coated coils shall receive a spray-applied, UV-resistant polyurethane topcoat to prevent UV degradation of the e-coat. Coating shall carry a 5 year warranty, from the date of original equipment shipment from the factory. The first 12 months from the date of equipment startup, or 18 months from the date of original equipment shipment from the factory, whichever is less, shall be covered under the standard AAON limited parts warranty. The remaining period of the warranty shall be covered by Luvata Electrofin.The Luvata Electrofin written instructions for installation, operation, coil cleaning, maintenance, and recording keeping must be followed. Refer to the Luvata Electrofin Terms and Conditions of Sale.

- Refrigeration System

- Unit shall be factory charged with R-410A refrigerant.

- Compressors shall be scroll type with thermal overload protection and carry a 5 year non-prorated warranty, from the date of original equipment shipment from the factory.

- Compressors shall be mounted in an isolated service compartment which can be accessed without affecting unit operation. Lockable hinged compressor access doors shall be fabricated of double wall, rigid polyurethane foam injected panels to prevent the transmission of noise outside the cabinet.

- Compressors shall be isolated from the base pan with the compressor manufacturer’s recommended rubber vibration isolators, to reduce any transmission of noise from the compressors into the building area.

- Each refrigeration circuit shall be equipped with expansion valve type refrigerant flow control.

- Each refrigeration circuit shall be equipped with automatic reset low pressure and manual reset high pressure refrigerant safety controls, Schrader type service fittings on both the high pressure and low pressure sides and a factory installed replaceable core liquid line filter driers.

- Unit shall include a variable capacity scroll compressor on all refrigeration circuits which shall be capable of modulation from 10-100% of its capacity.

- Lead refrigeration circuits shall be provided with hot gas reheat coil, modulating valves, electronic controller, supply air temperature sensor and a control signal terminal which allow the unit to have a dehumidification mode of operation, which includes supply air temperature control to prevent supply air temperature swings and overcooling of the space.

- Each refrigeration circuit shall include adjustable compressor lockouts.

- Each refrigeration circuit shall be provided with an adjustable temperature sensor freeze stat which shuts down the cooling circuits when the evaporator coil tubing falls below the setpoint.

- Condensers

- Air-Cooled Condenser

- Condenser fans shall be a vertical discharge, axial flow, direct drive fans.

- Coils shall be designed for use with R-410A refrigerant. Coils shall be multi-pass and fabricated from aluminum microchannel tubes.

- Coils shall be designed for a minimum of 10°F of refrigerant sub-cooling.

- Coils shall be hydrogen or helium leak tested.

- Condenser fans shall be VFD driven variable speed for condenser head pressure control.  Factory provided and factory programmed VFDs shall continuously modulate the fan air flow to maintain head pressure at acceptable levels. Cooling operation shall be allowed down to 35°F with adjustable compressor lockouts.

- Heating Coils

- Hot Water Heating Coils

- Coils shall be certified in accordance with AHRI Standard 410 and be hydrogen or helium leak tested.

- Coils shall be constructed of copper tubes with aluminum fins mechanically bonded to the tubes and galvanized steel end casings. Fin design shall be sine wave rippled.

- Coils shall be two rows, half serpentine circuitry, and 10 fins per inch.

- Coils shall be located in the reheat position downstream of the cooling coil.

- Control valves shall be factory supplied and field installed.

- Evaporator, hot water, and hot gas reheat coils shall have a flexible epoxy polymer e-coat uniformly applied to all coil surface areas without material bridging between fins. Humidity and water immersion resistance shall be up to a minimum 1,000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92). Corrosion durability shall be confirmed through testing to no less than 6,000 hours salt spray per ASTM B117-90. Coated coils shall receive a spray-applied, UV-resistant polyurethane topcoat to prevent UV degradation of the e-coat. Coating shall carry a 5 year warranty, from the date of original equipment shipment from the factory. The first 12 months from the date of equipment startup, or 18 months from the date of original equipment shipment from the factory, whichever is less, shall be covered under the standard AAON limited parts warranty. The remaining period of the warranty shall be covered by Luvata Electrofin.The Luvata Electrofin written instructions for installation, operation, coil cleaning, maintenance, and recording keeping must be followed. Refer to the Luvata Electrofin Terms and Conditions of Sale.

- Filters

- Unit shall include 2 inch thick, pleated panel filters with an ASHRAE efficiency of 30% and MERV rating of 8, upstream of the cooling coil.

- Unit shall include 0-100% economizer consisting of a motor operated outside air damper and return air damper assembly constructed of extruded aluminum, hollow core, airfoil blades with rubber edge seals and aluminum end seals. Damper blades shall be gear driven and designed to have no more than 20 cfm of leakage per sq. ft. at 4 in. w.g. air pressure differential across the damper. Low leakage dampers shall be Class 2 AMCA certified, in accordance with AMCA Standard 511. Damper assembly shall be controlled by spring return DDCactuator. Unit shall include outside air opening bird screen, outside air hood, and barometric relief dampers. Provide comparative enthalpy economizer sequence.

- Controls

- Isolation relays shall be factory installed.

- Provide full Linkspring DDC control platform with Indoor pool control sequence incorporating all items listed in this specification. Include Microsoft Surface with Wi-Fi Touch Screen interface with full graphics package including unit alarms, trend logging, control set point manipulation, monitoring, remote monitoring, and BACNET BMS interface to owner’s computer. Include refrigeration transducers for suction/discharge pressures/temperatures for all compressors.

- Accessories

- Unit shall be provided with a safety shutdown terminal block for field installation of a smoke detector which shuts off the unit's control circuit.

2.03 Curbs

- Provide minimum 57” tall double wall insulated plenum curbs with side SA/RA duct connections painted to match the unit

- Provide 3-sided service platform with 48” wide tread plate walkway, hand rail, knee rail, tow rail, ladder, and support structure for ease of unit service. Handrails to be removable for coil removal.

Part 3 - Execution

3.01 Installation, Operation, and Maintenance

- Installation, Operation, and Maintenance manual shall be supplied with the unit.

- Installing contractor shall install unit, including field installed components, in accordance with Installation, Operation, and Maintenance manual instructions.

Start up and maintenance requirements shall be complied with to ensure safe and correct operation of the unit

FINNED WATER-TUBE POOL HEATERS

PART 1 - GENERAL

  - SUMMARY

    - Section includes gas-fired, Cipro Nickel-finned tube pool heaters.

    - Related Sections

      - Building Services Piping – Division 23 21 00

      - Breeching, Chimneys, and Stacks (Venting) – Division 23 51 00

      - Electrical – Division 23 09 33

  - REFERENCES

    - ANSI Z21.56/CSA 4.7

    - ASME, BPV Section IV

    - 2006 UMC, Section 1107.6

    - ANSI/ASHRAE 15-1994, Section 8.13.6

    - National Fuel Gas Code, ANSI Z 223.1/NFPA 54

    - National Electrical Code, ANSI/NFPA 70

    - ASME CSD-1, 2009 (when required)

  - SUBMITTALS

    - Product data sheet (including dimensions, rated capacities, shipping weights, accessories)

    - Wiring diagram

    - Warranty information

    - Installation and operating instructions

  - QUALITY ASSURANCE

    - Regulatory Requirements 1.  ANSI Z21.56/CSA 4.7

2. Local and national air quality regulations for low NOx (< 20 PPM NOx emissions) pool heaters

- Certifications

  - CSA

  - ASME HLW Stamp and National Board Listed

  - HEAT EXCHANGER WARRANTY

    - Limited ten-year warranty from date of installation

    - Limited twenty-year thermal shock warranty from date of installation

PART 2 - PRODUCTS

  - POOL HEATERS

    - General

      - The pool heater(s) shall be fired with 990mbh gas at a rated input of 842mbh.

      - The pool heater(s) shall be CSA tested and certified with a minimum thermal efficiency of 85 percent at full fire.

      - The pool heater(s) shall be ASME inspected and HLW-stamped and National Board registered for 160 PSIG working pressure, complete with a Manufacturer's Data Report.

      - The pool heater(s) shall have a floor loading of 65 lbs. /square foot or less.

- Heat Exchanger

  - The heat exchanger shall be of a single-bank, horizontal-grid design with twelve integral Cipro Nickel-finned tubes, each end of which is rolled into an ASME boiler-quality steel tube sheet.

  - The heat exchanger shall be sealed to 160 PSIG rated brass headers with high temperature silicone "O" rings.

  - The low water volume heat exchanger shall be explosion-proof on the water side and shall carry a twenty-year warranty against thermal shock.

  - The headers shall be secured to the tube sheet by stud bolts with flange nuts to permit inspection and maintenance without removal of external piping connections. The heat exchanger shall incorporate "V” baffles between the tubes to ensure complete contact of the external tube surfaces with the products of combustion.

  - The pool heater(s) shall be capable of operating at inlet water temperatures as low as 105°F without condensation.

  - The pool heater(s) shall be designed to accommodate field changes of either left or right hand plumbing and electrical while leaving the tube bundle in place.

- Burners

  - The tubular burners shall have multiport radial gas orifices, punched ports and slots, be capable of quiet ignition and extinction without flashback at the orifice, and be manufactured from corrosion-resistant titanium-stabilized stainless steel with low expansion coefficient.

  - The burners will be supplied with a fan-assisted, clean burning, and highly efficient fuel-air mixture.

- Ignition Control System

  - The pool heater(s) shall be equipped with a 100 percent safety shutdown system.

  - The ignition shall be Hot Surface Ignition type with full flame rectification by remote sensing separate from the ignition source, with a three-try-for-ignition sequence, to ensure consistent operation.

  - The igniter will be located away from the water inlet to protect the device from condensation during startup.

  - The ignition control module shall include an LED that indicates six (6) individual diagnostic flash codes.

  - Two external viewing ports shall be provided, permitting visual observation of burner operation.

- Gas Train

  - The pool heater(s) shall have a firing/leak test valve and pressure test valve as required by CSD-1.

  - The pool heater(s) shall have dual-seated main gas valve(s).

  - Gas control trains shall have a redundant safety shut-off feature, main gas regulator, shut-off cock and plugged pressure tapping to meet the requirements of ANSI Z21.56/CSA 4.7.

- Pool Heater Control

  - The following safety controls shall be provided:

    - High limit control

    - Flow switch, mounted and wired

    - 125 PSIG ASME pressure relief valve, piped by the installer to an approved drain

    - Temperature and pressure gauge

    - Poolstat

  - The pool heater(s) shall be equipped with an energy-saving pump relay, mounted and wired, which automatically shuts off the pool heater pump at a set period after pool heater shut-down

Table for five or ten minutes) to avoid standby losses associated with constant pump operation.

G. Firing Mode

1. For all models, provide on-off firing control of the gas input to the pool heater.

- Pool Heater Diagnostics

  - Provide external LED panel displaying the following pool heater status/faults:

    - Power on - Blue

    - Call for heat – Amber

    - Flow - Green

    - Stages 1,2, 3 and 4 – Green

    - Fans 1, 2, and 3 proven - Green

    - Ignition fault - Red

    - Safety fault - Red

  - Provide internal circuit board indicating the following safety faults by a 2-line, 20-character LCD display:

    - System status

    - Manual reset high limit

    - Auto reset high limit

    - Blocked vent switch

    - Low gas pressure switch

    - Flow switch

    - Air pressure switch

    - Factory option

    - External interlock

    - Ignition lock-out

    - Auto reset high limit

    - Low water cut-off

    - High gas pressure switch

    - Controller alarm

    - Cold Water Run

  - A Central Point Wiring board with diagnostic LED’s indicating the status of each relay.

  - Provide ignition module indicating the following flash codes by LED signal and displayed on the LCD display:

    - 1 flash – low air pressure

    - 2 flashes – flame in the combustion chamber w/o CFH

    - 3 flashes – ignition lock-out (flame failure)

    - 4 flashes – low hot surface igniter current

    - 5 flashes – low 24VAC

    - 6 flashes – internal fault (replace module)

- Combustion Chamber: The lightweight, high temperature, multi-piece, interlocking ceramic fiber combustion chamber liner shall be sealed to reduce standby radiation losses, reducing jacket losses and increasing unit efficiency.

- Venting

  - When routed vertically, the pool heater’s flue material and size shall be in accordance with the National Fuel Gas Code, ANSI Z223.1/NFPA54 latest edition (Category I).

  - When routed horizontally, the pool heater’s flue material and size shall meet or exceed the requirements as specified for Category III in the National Fuel Gas Code, ANSI Z223.1/NFPA 54 latest edition.

  - The pool heater(s) shall be ducted combustion air ready.

- Cabinet

  - The corrosion-resistant galvanized steel jackets shall be finished with a baked-on epoxy powder coat, which is suitable for outdoor installation, applied prior to assembly for complete coverage, and shall incorporate louvers in the outer panels to divert air past heated surfaces.

  - The pool heater(s), if located on a combustible floor, shall not require a separate combustible floor base.

  - The pool heater(s) shall have the option of venting the flue products either through the top or

the back of the unit.

4. Combustion air intake shall be on the left side of the cabinet, right side optional.

- Manual Bypass

  - The heater shall be equipped with an external bronze pump and bypass arrangement designed to maintain the water entering the heater at the proper temperature that will prevent condensation and scale in the heat exchanger. The entire waterway shall be non-ferrous.

- Pool Heater Pump

- Cold Water Run System

  - The pool heater(s) shall be configured with a cold water run automatic proportional by-pass system that ensures the pool heater will experience inlet temperatures in excess of 105ºF in less than 7 minutes to avoid damaging condensation. The unit will automatically shut down if the inlet temperature is not achieved within the 7 minute time frame.

  - The cold water run system shall be configured with a variable speed pump that is controlled by a system-matched PID control that injects the correct amount of cold water directly into the - pool heater loop to maintain a minimum inlet temperature. The PID controller temperature sensor shall be located in the inlet header of the pool heater.

  - The control shall have a temperature setting dial located on the face of the board. The temperature range of the dial shall be 105ºF to 120ºF. The PID Logic shall be capable of limiting system overshoot to a maximum of 10ºF on initial start-up or call-for-heat.

  - The cold water run system shall be completely wired and mounted at the factory.

  - The control shall have the following diagnostic LED’s:

    - Call for heat

    - Start-up mode

    - Inlet temperature error

    - Sensor out of range

  - The controller shall have alarm contacts.

- TruSeal™ Direct Vent

  - The pool heater(s) shall meet safety standards for direct vent equipment as noted by the 2006 UMC, section 1107.6, ASHRAE 15-1994, section 8.13.6, and ANSI Z21.56/CSA 4.7.

  - SOURCE QUALITY CONTROL

    - Pool heater(s) shall be completely assembled, wired, and fire-tested prior to shipment from the Factory.

    - The pool heater(s) shall be furnished with the sales order, ASME Manufacturer’s Data Report,

inspection sheet, wiring diagram, rating plate and Installation and Operating Manual.

PART 3 - EXECUTION

  - INSTALLATION

    - Must comply with:

      - Local, state, provincial, and national codes, laws, regulations and ordinances

      - National Fuel Gas Code, ANSI Z223.1/NFPA 54 – latest edition

      - National Electrical Code, ANSI/NFPA 70 – latest edition

      - Standard for Controls and Safety Devices for Automatically Fired Boilers, ANSI/ASME CSD-1, when required

      - Canada only: CAN/CSA B149 Installation Code and CSA C22.1 CEC Part I

      - Manufacturer’s installation instructions, including required service clearances and venting guidelines

    - Manufacturer’s representative to verify proper and complete installation.

  - START-UP

    - Shall be performed by Raypak factory-trained personnel.

    - Test during operation and adjust if necessary:

      - Safeties (2.2 - F)

      - Operating Controls (2.3)

      - Static and full load gas supply pressure

      - Gas manifold and blower air pressure

    - Submit copy of start-up report to Architect and Engineer.

  - TRAINING

    - Provide factory-authorized service representative to train maintenance personnel on procedures and schedules related to start-up, shut-down, troubleshooting, servicing, and preventive maintenance.

    - Schedule training at least seven days in advance.

ALTERNATE #1

      - Provide a deduct for if Owner purchased equipment directly from Manufacturer.