QUESTIONS:

1.)   On drawing E301 note 1, it says that we are to verify if the existing conduits

are sized right as per the wire size called for on the same drawing.

I will have to refer this question back to the engineer and ask him if the

existing 3" pvc schedule 40 conduits are acceptable or not using the

4- 350 mcm and 1-#1 copper wires that are shown to be installed in

each of the 2 existing conduits. Please let me know if the conduits are

acceptable or do they need to be a increased in size to handle the wire

called for.  Yes, the existing 3” conduit is acceptable for wire sizes shown.

2.)  What is the 3" conduit to be used for that runs along the back wall

behind the floor drain on sheet E201.

We can only assume that it may be the feeder conduit for Panel PA2,

but it is not drawn as so.  Yes, it is the feeder to panel ‘PA2’.

3.) I am not clear about what note 1 on sheet E201 is saying about the Nema 3R

Junction box. Is this Nema 3R junction box being furnished with all the items

such as the distro, cam locks and the direct connect materials furnished by

others or do we furnish it with a not to exceed $3,000.00 allowance.

Contractor to furnish using a $3000 allowance. The allowance is to cover the NEMA 3R box and the branch circuiting only. The distro boxes, etc. are to be provided by others.