City of Lebanon

Request for Proposal

RFP # 19-MOTOR CONTROLS 3/21
*City of Lebanon reserves the right to reject all or any part of any RFP*

The City of Lebanon is exempt from State Tax and Federal Exercise Tax.

NO PROPOSALS RECEIVED AFTER CLOSING WILL BE ACCEPTED.

The City of Lebanon invites sealed proposals for motor controls, in accordance with the specifications and bidding instructions set forth in this Request for Proposals. Bids will be received by the Purchasing Department, 200 N. Castle Heights Avenue, Lebanon, Tennessee 37087, until 10:00 a.m. local time, March 21, 2019, at which time they will be opened and read aloud.

Please identify as a sealed proposal with stamped on the outside of the envelope “RFP #19-MOTOR CONTROLS 3/21”

Any questions in regard to this proposal should be directed to Lisa Lane, Purchasing Agent, (615) 443-2802.

A copy of the bid tabulation will be available upon written request to the Purchasing Department.

Any manufacturers’ names, trade names, brand names, or catalog numbers used in the specifications are for the purpose of describing and establishing general quality levels.  Such references are not intended to be restrictive.  Since the “City” does not wish to rule out other competition and equal brands or makes, please remember “ANY APPROVED EQUAL”.  HOWEVER, IF A PRODUCT OTHER THAN SPECIFIED IS BID, IT IS THE VENDORS RESPONSIBILITY TO PROVE TO THE “CITY” THAT SAID PRODUCT IS EQUAL TO OR EXCEEDS THE QUALITY OF THE SPECIFICATIONS LISTED FOR ANY ITEM.

The City of Lebanon is an equal opportunity entity and does not discriminate on the basis of age, race, sex, national origin, religion or disability in admission to, access to, or operations of its programs, services, activities, or in its awarding of such bids.

1. SCOPE AND CLASSIFICATION

1.1 Scope:  The intent of this Request for Proposals and resulting contract is to provide the City of Lebanon with information concerning motor controls.

1.2 Classification:  The motor controls specifications shall be of the following types either “equal to “or “better than”.

2. SPECIFICATIONS

Replacement of 2-75 HP Auto Transformer Motor Controls
City of Lebanon Tennessee Water Treatment Plant

 Location:  7 Gilmore Hill Road, Lebanon, TN  37087 

Raw Water Intake
Purpose:  The purpose of this document is to explain work description and job requirements for the purpose of acquiring bids for the replacement of (2) 75 HP Pump control centers/systems to modern Soft Start controls technologies located at the Lebanon Tennessee, Water Treatment Plant Facility for the raw water intake pumps.

Scope of work:

Overview:

To remove two existing auto transformers and motor starter control systems, then replacing with new soft starters for controlling (2) 75 hp pump motors which are located at the Raw Water Intake Building.

Specifications:

1. Removal of old equipment and hardware.  Scope to include removing all existing controls and auto-transformers located in each of the (2) motors control cabinets.  Existing Cabinets to remain and be reused.  
2.   Scope includes the removal of any existing wiring that does not meet current NFPA and NEC requirements for location and equipment size and horse power/current ratings.  Scope includes replacing any wiring and connection points and terminals/lugs etc. that do not meet or exceed NEC and NFPA requirements.

3.   Scope includes the purchase and installation of new back-plane hardware and all accessories to house or hold the new soft starts and any relays or other necessary hardware for controlling each pump motor for both electrical cabinets.

4.   Scope also includes the purchase and installation of (2) new soft starters.  Soft starters are to be Square D brand or an equivalent quality brand.

5.   Scope includes wiring and programming of soft starters to operate per the requirements of the pump system and water plant operations, to include interfacing with existing PLC for start, stop, and run and alarm statuses.

6.   Scope to include wire labels for each wire in the cabinet and to include all documentation of electrical schematics and/or prints in both digital and paper media.  (Preferred digital media is .dwg and .pdf formats for all drawings.)

7.   The documentation provided by winning bid company to include any manuals or cut sheets for both of the soft starters and for any necessary controls hardware inside of electrical cabinets.

8.   HIM (Human Interface Module) or OIM (operator interface module) shall be mounted on the outside of the electrical panel doors with all cabling to be securely mounted in a way to not snag, droop or in any way interfere with door opening and closing properly.

9.   Winning bid contractor to provide training to plan personnel in regards to operation and navigation through the user interface of soft starter HIM module, and basic theory of operation.

10.   The winning bid contractor must follow all safety guidelines such as lock-out tag-out safe work practices.  All breakers and other power sources to be powered off and secured to ensure no power is reestablished inadvertently while project is ongoing which could cause injury, death, and/or property damage.

11.   Winning bid contractor is responsible for the removal of any trash or demoed material, with exception to any salvageable materials such as transformers or old wiring.  This material is to be set aside for Lebanon Water Plant personnel to pick up after job is completed.
12.   Bidders must schedule and on-site visit with either J.C. York or Greg Anderson to verify installation location and answer any questions concerning the scope of work prior to the bid opening date and time.  Contact Phone Number (615) 444-0485.

13.   Bid must include all labor, parts, shipping, training, etc. in the bid price.  

14.   The awarded vendor must schedule installation of the motors with J.C. York and/or Greg Anderson.

15.   Please state your warranty period and a description of what is covered in the warranty.  (Attach separate sheet describing warranty).

QUANTITY
DESCRIPTION

UNIT COST

TOTAL
2 

75 HP Auto Transformer 

Motor Controls

$_____________
$_____________

2

Parts &Labor

$_____________
$_____________

1

Shipping Charges

$_____________
$_____________

1

Total



$_____________
$_____________
3. WARRANTY 

Bidders shall state the warranty period on the bid pricing form.  

4. INSTALLATION
The vendor must state their expected installation date. 

5. EXCEPTIONS

The above are minimum specifications.  If there are any exceptions to these specifications, please make any notations to the right of that spec. and the exceptions will have to be approved by the department.  

6. BID PRICE

TOTAL BID $_______________________

     
6.2    INSTALLATION   _____________________

Company Name and Authorized Representative

______________________________________________________________

Address and Contract Phone Number

Include:

Proof of Liability Insurance, Worker’s Comp., Contractor’s License, Business License.
