{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":13,"n_cols":3,"rows_kept":13,"merged":[[0,0,0,2],[1,0,1,2]]}
["Vendor Name:  ____________________________"]
["Exhibit A - Price Sheet"]
["School","Scope of Works","Cost"]
["Anderson County High School","Five-year mandatory inspection.  Replace 17 brass uprights on riser #1, replace bad gauges on riser #1, add an inspector test on riser #1, take sample of QR CH pendants from riser #2 and send them off for UL head testing, plug off bell lines to the inoperable water motor gong and provide an electric bell.  Will require 26' Scissor Lift Rental."]
["Clinch River Community School","Five-year mandatory inspection.  Extend 4 heads to fit the ceiling properly, replace bad 4\" flow switch"]
["Clinton High School","Five-year mandatory inspection.  Replace 3 missing escuthcheons, replace bad tamper switch on system #3, replace 14 pendant heads in kitchen, replace 2 dry sidewall heads and 4 dry pendant heads in lieu of UL Head testing, plug off bell lines to the inoperable water motor gong and provide an electric bell."]
["Lake City Elementary School","Five-year mandatory inspection.  Replace 7 missing escuthcheons, replace 2 painted heads to extend to 3 heads to fit the ceiling properly,  replace all heads in kitchen prep area, replace 6 dry pendant heads in lieu of UL Head testing them, install dry pendant heads in the proper fittings and to plug off lines to the inoperable water motor gong and provide an electric bell."]
["Grand Oaks Elementary School","Five-year mandatory inspection.  Replace bad PIV tamper switch on wet system #1, attempt to unseize the PIV at the pit, provide spare heads for the heads box, replace two recalled dry pendants in the freezer, replace a corroded pendant in laundry room and extend it to fit the ceiling, extend 3 heads in the dishwasher room, replace the 4 older upright heads in boiler room, replace the painted pendant head in the gym, attempt to unclog the inspectors test."]
["Claxton Elementary School","Replace the bad 1# threaded flow switch."]
["ACCTC","Take sample of brass uprights and chrome pendants to send them off for UL head testing, replace the broken angle valve, pipe the auxillary drain back out the wall, plug ogg the inoperable water motor gong and provide electric bell."]
["Norris Middle School","Five-year mandatory inspection.  Replace missing escutcheons, extend 2 heads to fit the ceiling properly, replace corroded head in the stairwell, replace bad globe valve in mens lock room gym, take samples of QR Chrome pendants and send them off for UL Head testing, perform annual oil change on the air compressor, plug off bell lines to the inoperable water motor gong and provide an electric bell."]
["Fairview Elementary School","Replace broken 2\" main drain on riser #1, replace the 2 painted heads on the gym stage, extend 1\" head in kitchen to fit the ceiling properly, provide spare heads for the head box."]
["Norwood Middle School","Five-year mandatory inspection.  Extend 5 pendant heads to fit the ceiling properly, replace a missing escuthcheon in boys restroom, reinstall the hanger to pull one head into the proper position."]