City of Myrtle Beach

Request For Proposal

RFP 18-R0030

Fire Safety Maintenance for Fire Alarm System, Sprinklers System, Fire Extinguishers and Exhaust Hoods

Issue Date:  May 4, 2018

First in Service

Issued By:

Purchasing Division

3231 Mr. Joe White Avenue

Myrtle Beach, SC  29577

Phone:  843-918-2170

www.cityofmyrtlebeach.com

City of Myrtle Beach Purchasing Division

3231 Mr. Joe White Avenue

Myrtle Beach, SC  29577

| REQUEST FOR PROPOSAL |  |
| --- | --- |
| RFP # 18-R0030 |  |
| Buyer Contact: | Tina Causey 843-918-2184 tcausey@cityofmyrtlebeach.com |
| Mandatory Pre-Proposal Conference: Attendance is required for proposal consideration | Tuesday, May 15, 2018 @ 10:00 Myrtle Beach Convention Center 2101 N Oak Street Myrtle, Beach, SC Meet in front lobby next to escalator |
| Opening Date & Time: | Tuesday, May 22, 2018 at 2:00PM |

Please note the following required condition (if indicated by an X below):

______ Proposal for a service $20,000.00 or greater must be accompanied by a bid bond in the amount of five percent (5%) of the total dollar amount of the proposal submitted, payable to the City of Myrtle Beach.

No proposals will be accepted unless submitted on the forms furnished herein.  All pages of the proposal must be in a sealed envelope and delivered in accordance with these instructions:

- The envelope must be marked with company name, proposal number/name, and time/date of proposal opening.

- Proposal packages shall be delivered to the address listed above.  The City of Myrtle Beach is not responsible for late or misdirected mail.

If the above criteria are not met, your proposal may be rejected.  Proposals are not subject to public reading.

Offerors are advised that from the date of issue of this solicitation until award of the contract, no contact with City personnel related to this solicitation is permitted.  All communications/requests for clarification are to be directed to the Buyer listed above.

It is the intent and purpose of the City of Myrtle Beach that this Request for Proposal promotes competitive proposals.  It shall be the Offeror’s responsibility to advise the Purchasing Division if any language, requirements, etc., or any combination thereof, inadvertently restricts or limits the requirements stated in this Request for Proposal to a single source.  Such notification must be submitted in writing and must be received by the Purchasing Division no later than three (3) City of Myrtle Beach business days prior to the proposal opening date.

Offeror to complete this section:

Name of Offeror:	________________________________________________________________________

Address:	______________________________________________________________________________

PhoneNumber:_____________________________________________________________

E-mail:	:_______________________________________________________________________________

Please note:  Signature is required on page 17.

CITY OF MYRTLE BEACH – GENERAL INSTRUCTIONS

MUST BE SIGNED AS PART OF REQUEST FOR PROPOSAL PACKAGE

1.0	SUMMARY/SPECIFICATION

  - DOCUMENT INCLUDES:

2.0	Authority

2.01		Equal Weight and Force

2.02		Written Explanations

2.03		Disputes with Written Explanations

2.04		Written Addenda

3.0	Requirements for Written Proposal Documents

3.01		Availability of Documents

3.02		Non-Responsive Proposals

3.03		Document Completion

3.04		Contents of Proposal Packet

3.05		Single Package Requirement

3.06		Proposal Submission

3.07		Proposal Delivery/Opening

3.08		Document Ownership

4.0	Full Examination

4.01		Thorough Investigation

4.02		Pre-Proposal Meetings

4.03		Evidence of Examination

5.0	Pricing

5.01		Unit Pricing

5.02		Cash Discounts

5.03		Changes in Cost

6.0	Tax Information

6.01		Sales Tax/Federal Tax

6.02		Payment of Taxes

7.0	Material Assessment

7.01		Product Documentation

7.02		MSDS

7.03		Evidence of Work/Product

7.04		Sample Submission

7.05		Sample Ownership

7.06		Furnished Items

7.07		Quality of Items

8.0	Changes in Specifications

8.01		Authority of Specifications

8.02		Equipment

8.03		Deviation from Specifications

8.04		Material Preference

8.05		Changes after Award

8.06		Equivalent Items

9.0	Modifications

9.01		Additional Work

9.02		Adjustments to Items/Work

10.0	Bond Requirements

10.01		Proposal/Performance/Payment Bonds

11.0	Delivery

11.01		Warehouse Deliveries

11.02		Dates

11.03		Delivery Price

11.04		Documentation

11.05		Wrong Deliveries

12.0	Award Criteria/Timeline

12.01		Award Criteria

12.02		Contract Issuance

12.03		Contract Timeline

12.04		Notification

13.0	Offeror Responsibilities

13.01		Duration of Proposal

13.02		Transfer of Responsibilities

13.03		Subcontractors

13.04		Coordination and Contact

13.05		Liquidated Damages

14.0	Indemnity Clause

14.01		Hold Harmless

15.0	Federal and State Laws

15.01		Employment Regulations

16.0	Financial Accounting

16.01		Representation

16.02		Payment

17.0	Proposal Rejection/Withdrawal

17.01		Reasons for Rejection

17.02		Best Interest

17.03		Withdrawal Timeline

18.0	Protest Procedures/Timelines

18.01		Proposal Specifications/Contract Terms

18.02		Intent to Award

19.0	City Reserved Rights

19.01		Reserved Right

19.02		Final Judgment

19.03		Clarification

19.04		Price Increase

19.05		Loss/Damage

19.06		Performance Failure

19.07		Negotiation

20.0	ADA Compliance

20.01		Contact Information

21.0	Signatures

21.01		Accuracy and Completeness

21.02		Compliance

  - DEFINITIONS:

- City of Myrtle Beach – herein referred to as “City.”

B.  RFP – Request for Proposal

C.  Offeror – any vendor, proprietor, business, company, service provider, or corporation who submits a proposal to the City.

D.  Proposal – the collection of documents that includes these general instructions,           the scope of work and/or specifications, a written offer, and signature page to

be used for consideration in negotiations and/or contract development.

E.  Addendum – a written change, addition, alteration, correction, or revision to a proposal document.

F.  Bond – provides financial assurance that the proposal has been submitted in good faith, that a offeror will enter into a contract at the amount proposed, and will

provide the appropriate performance and payment bonds.

G.  Bid Bond – an insurance agreement, accompanied by a monetary commitment, by which a third party accepts liability and guarantees that the bidder will not

withdraw from the bid.

H.  Performance Bond – guarantees execution of the terms of a contract.

I.  Payment Bond – covers payment of subcontractors, laborers, and materials suppliers associated with the project.

2.0	AUTHORITY:

2.01	Equal Weight and Force.  The instructions herein contained are given for the purpose of guidance in properly preparing an applicable proposal.  These directions have equal weight and force with the specifications and strict compliance is required with all of the provisions.

Unless otherwise stated in the special instructions of the proposal, these general

instructions will apply.

2.02	Written Explanations.  Only written information from the procurement manager or an authorized representative of the purchasing division is binding; therefore no verbal instructions or verbal information from any other source will be binding on the City.  The 	City will not be responsible for any other explanation or interpretation and the decision of the procurement manager or an authorized representative of the purchasing division shall be final and binding upon each Offeror.

2.03	Disputes with Written Explanations.  The written specifications are considered clear and complete.  Failure of the Offeror to call attention in writing to any disputes, definitions, discrepancies, inconsistencies or incompleteness before the opening of the proposal in the time and manner set forth herein is a waiver of right to do so upon opening of the proposals.

Clarifications requested by Offerors must be in writing not less than three (3) days before 	date and time set for receipt of proposals.

2.04	Written Addenda.  Should the procurement manager deem it necessary to alter proposal specifications, those alterations will be made in the form of written addenda that will be posted on the City website.  The Offeror is responsible for monitoring the website. These addenda shall then be considered as part of these specifications.

3.0	REQUIREMENTS FOR WRITTEN DOCUMENTS:

3.01	Availability of Documents.  Proposal documents may be obtained through the City of Myrtle Beach website (www.cityofmyrtlebeach.com), or in person at the City of Myrtle 	Beach Purchasing Office, 3231 Mr. Joe White Avenue, Myrtle Beach, SC  29577, Monday through Friday (excluding City holidays), from 8:00 AM to 5:00 PM.  Proposal documents may be mailed or sent via e-mail by vendor request only.

3.02	Non-Responsive Proposals.  Proposals that are incomplete, unsigned, improperly signed 	or sealed, conditional, illegible, obscure, contain arithmetical errors, erasures without initials, alterations or irregularities of any kind, may be declared non-responsive.

3.03	Document Completion.  A proposal and signature document is provided as part of the  solicitation.  This form must be used in submitting a proposal and all pages of the proposal document must be completely filled out and signed by the Offeror.  No proposal will be accepted unless submitted on the forms furnished herein.  Erasures or corrections made on the proposal documents prior to submission must be initialed by the Offeror.

3.04	Contents of Proposal Packet.  The general instructions, scope of work and/or

specifications, and the proposal and signature document constitute the proposal packet. By submitting a proposal, the Offeror is deemed to have accepted all of the terms and conditions set forth in the proposal packet documents.  All proposal packet documents, after completion by the Offeror, must be returned with the proposal in the same order as 	received by the Offeror.

3.05	Single Package Requirement.  Unless otherwise stated in the special instructions section of this proposal request, submit one complete proposal package using the attached form(s), if applicable, for proposed pricing.

3.06	Proposal Submission.  Each proposal must be enclosed in a sealed envelope, clearly 	marked on the outside with information as stated on the cover page and delivered to the procurement buyer.  If the required information is not clearly stated on the outside of the envelope, the proposal is considered nonresponsive.  Proposals submitted after the date and time set for receipt will be returned to the Offeror unopened.

3.07	Proposal Delivery/Opening.  All proposals must be sealed, marked and delivered in accordance with these instructions to Purchasing Division, City of Myrtle Beach,

3231 Mr. Joe White Avenue, Myrtle Beach, SC  29577.  Proposals are not subject to a formal proposal opening.

3.08	Document Ownership.  All documents, reports, proposals, submittals, working papers or other material submitted to the City from the Offeror shall become the sole and exclusive property of the City, in the public domain, and are not the property of the Offeror.  The 	Offeror shall not copyright, or cause to be copyrighted, any portion of any of said documents submitted to the City as a result of this solicitation.

4.0	FULL EXAMINATION:

4.01	Thorough Investigation.  Offerors shall make all investigations necessary to thoroughly inform themselves regarding plant and facilities for delivery of material and equipment and/or service to be performed as required by the proposal conditions.  No plea of ignorance by the Offeror of conditions that exist or that may hereafter exist as a result of failure or omission on the part of the Offeror to make the necessary examination and investigations, or failure to fulfill in every detail the requirements of the contract documents, will be accepted as a basis for varying the requirements of the City or the compensation.

4.02	Pre-Proposal Meetings.  When Offerors are required to make site visits or attend

pre-proposal meetings, all expenses shall be paid for by the Offeror, unless previous written arrangements are made with the City.  No offeror will be admitted to a pre-proposal meeting after the specified start time, otherwise the proposal will be considered non-responsive.

4.03	Evidence of Examination.  Submission of a proposal will be considered as conclusive evidence of the Offeror’s complete examination, understanding and acceptance of the specifications.

5.0	PRICING:

5.01	Unit Pricing.  Unit pricing will govern over extended prices unless otherwise stated in special instructions in this proposal request.  All prices quoted should be firm.  In those cases where a firm proposal cannot be made, consideration will still be given to all Offerors.  Also, maximum or ceiling prices should be quoted where possible when proposal contain non-firm prices.

5.02	Cash Discounts.  Cash discounts, if allowed, should be so stated on the proposal form.  	Prices must, however, be based upon payment thirty (30) calendar days after delivery.

5.03	Changes in Cost.  If during the term of the contract entered into as a result of this proposal, the cost of material(s) is/are increased through no act on the part of the contractor other than to comply with any prevailing rise in the market price(s) of material(s) used, it shall be the contractor’s responsibility to notify the City of Myrtle Beach Purchasing Office in writing of the price increase(s) and the effective date of the increase(s).  Price(s) shall be increased only to the point of absorbing additional cost(s) of material(s) paid for by the contractor.  At any time during the term of the contract, the City may request that the contractor provide written documentation from the manufacturer/supplier of the material(s) to substantiate price increase(s).  If during the term of the contract, the cost of material(s) 	to the contractor is reduced, then the contractor shall reduce the contract price(s) and notify 	the procurement buyer in writing.

6.0	TAX INFORMATION:

6.01	Sales Tax/Federal Tax.  The City of Myrtle Beach pays South Carolina State Sales Tax. 	The City is exempt from Federal Excise Tax and will issue exemption certificates if required.  All applicable taxes should be shown as separate line items unless otherwise indicated.

6.02	Payment of Taxes.  The contractor agrees to pay all taxes and license fees of whatever nature applicable to conduct business and furnish the City of Myrtle Beach, if requested, with duplicate receipts or other satisfactory evidence showing the prompt payment of all taxes and fees when referred to and showing that all licenses are in effect.

7.0	MATERIAL ASSESSMENT:

7.01	Product Documentation.  Proposal shall include adequate brochures, latest printed

specification and advertising literature describing the product(s) offered in such a fashion as to permit ready comparison with the specifications on an item-by-item basis where applicable.

7.02	Materials Data Safety Sheet (MSDS).  If so requested in the proposed documents, a completed MSDS for the item(s) indicated must be provided with the proposal documents.  Failure to submit this form upon request may result in rejection of proposal.

7.03	Evidence of Work/Product.  All Offerors must be prepared to present suitable evidence of similar work recently completed or goods supplied.  Products are to be brand name or equal unless otherwise specified. If submitting an equal product, supporting documents must be provided with proposal.

7.04	Sample Submission.  When samples are required with a proposal, they must be submitted with the proposal unless approved by the purchasing manager or purchasing manager’s authorized representative.

7.05	Sample Ownership.  Samples submitted will become the property of the City of Myrtle 	Beach.  The entire cost of the sample(s) shall be paid for by the Offeror unless previous written arrangements are made with the City.

7.06	Furnished Items.  Offerors are required to state exactly what they intend to furnish;

otherwise, they shall be required to furnish the items as specified.

7.07	Quality of Items.  Offerors will submit, with their proposal, data necessary to evaluate and determine the quality of the item(s) they are proposing.

8.0	CHANGES IN SPECIFICATIONS:

8.01	Authority of Specifications.  It shall be understood that in all cases the terms and

conditions, as detailed in the specifications, shall supersede terms and conditions, as detailed in the general instructions.

8.02	Equipment.  If this proposal is for the purchase of equipment, the Offeror guarantees that the equipment offered is standard new equipment, latest model or regular stock product, 	with parts regularly used for the type of equipment offered; also that no attachment or part has been substituted or applied contrary to the manufacturer’s recommendations and standard practices.

8.03	Deviation from Specifications.  Any deviation from specifications must be noted in detail and submitted in writing with this proposal.  Complete specifications should be attached for any substitutions offered, or when amplifications are desirable or necessary.  The absence of a specification deviation statement and accompanying specifications will hold the Offeror strictly accountable to the specifications as written herein.

8.04	Material Preference.  The specifications, as listed herein, represent our preference in material; however, we are fully cognizant that no two pieces of comparable material are identical and/or same in size, function, and operation; and some of the specifications will not completely coincide with ours as listed.  Please list your exceptions and explanations separately. It is not our intent to write specifications for any project on which only one proponent can submit a proposal.

8.05	Changes after Award.  Any changes in specifications, after the purchase order/contract 	has been awarded, must be with the written consent of the purchasing division; otherwise, the responsibility for such changes shall be with the Offeror.

8.06	Equivalent Items.  When brand names or trade names and model numbers followed by the words "or equivalent" or "or other approved equal" are used, it is for the quality, style and features of those brands and models.  Proposals on equivalent items of substantially the same quality, style and features are then invited.  However, to receive consideration, 	such equivalent proposals must be accompanied by sufficient descriptive literature and/or specifications to clearly identify the units and provide for competitive evaluation with the brands or models.

9.0	MODIFICATIONS:

9.01	Additional Work.  No extras or additional work will be allowed or paid for unless such extras or additional work are/is ordered in writing by the purchasing division and with the price for such established and agreed upon before such extras are delivered or work is performed.

9.02	Adjustments to Items/Work.  The City of Myrtle Beach shall have the right, without invalidating the contract, to make additions to or deductions from the items or work covered by the specifications.  In case such deductions or additions are made, an equitable price adjustment shall be made between the City and the contractor.  Any such adjustments in price shall be made in writing.

10.0	BOND REQUIREMENTS:

10.01	Proposal/Performance/Payment Bonds.  If required, Offeror shall supply a proposal bond of 5% of the total proposal amount.  The successful Offeror at its own cost and expense shall furnish, if required, a valid performance and payment bond (payable to the City of Myrtle Beach) in the full amount of this agreement conditioned on the full and faithful performance of the work under this agreement in accordance with the specifications and contract documents.  Bonds are required if the contract work is valued 	at $20,000.00 or more for construction and/or any type of service related requirement. The performance and payment bonds shall be executed by the contractor and a bonding company authorized to do business in the State of South Carolina and approved by the 	State of South Carolina to issue such performance and payment bonds.  Only the forms provided by the City for the performance and payment bonds will be accepted.

11.0	DELIVERY:

11.01	Warehouse Deliveries.  Unless otherwise stated in the special instructions section of this 	proposal request, deliveries will be accepted during the hours between 8:00 AM and 4:00 PM Monday through Friday, excluding City holidays.

11.02	Dates.  The delivery date as stated in the proposal shall be the time required to deliver the complete item(s) after the receipt of the order or award of the contract.  Where multiple items appear on a proposal request, the Offeror shall, unless otherwise stated by the City, 	show delivery date for each item separately.  If only a single delivery date is shown, it will be assumed to mean that all items included in the proposal can and will be delivered on or before the specified date. The Offeror certifies that the delivery will be completed in the time the Offeror states, starting at the time the order is placed, provided that the time between the proposal opening and the placing of the order does not exceed the number of 	days stipulated in the proposal.  The right is reserved to reject any proposal on which the 	delivery time indicated is considered sufficient to delay the operation for which the commodity is intended. Successful Offeror(s) will be responsible for making any and all

claims against carriers for missing or damaged items.

11.03	Delivery Price.  Proposal prices are to be Delivered Price (FOB Destination).  Proposal prices must include all delivery costs, including but not limited to, loading and unloading 	cost(s), transportation charge(s) and fuel surcharge(s).  The City of Myrtle Beach will not be responsible for any demurrage charge(s).

11.04	Documentation.  Invoice(s), certificates of origin, warranties and guarantees must be submitted at the time of delivery of the item(s).

11.05	Wrong Deliveries.  In the event that materials, supplies, etc. are delivered which do not 	comply with specifications and have not been approved by the purchasing division, the contractor, upon notification, shall immediately remove from the premises any such materials, supplies, etc. and replace them with materials, supplies, etc. in full accordance with the specifications.

12.0	AWARD CRITERIA/TIMELINE:

12.01	Award Criteria.  The award will be made within the time specified to the responsible Offeror meeting the specifications and having the lowest possible cost consistent with the quality and service needed for effective use.  The following criteria will be used in making this determination:

A.  Superior quality and specification adherence

B.  Adequate maintenance and service

C.  Delivery and/or completion time

D.  Guarantees and warranties

E.  Company’s reputation and financial status

F.  Past experience and cost with similar or like equipment or service

G.  Anticipated future cost and experience

H.  Performance of proponent’s equipment by other agencies, plants, and firms Evaluation factors, if required, shall be stated in either a percent basis or a numerical format.

12.02	Contract Issuance.  The award of a contract is accomplished by executing a written agreement that incorporates the entire proposal, Offeror’s response, clarifications, addenda, and additions.  All such materials constitute the contract documents.  The Offeror agrees to accept the contract terms unless substantive changes are made without the approval of the Offeror.  The procurement office is the sole point of contact for the issuance of the contract.

12.03	Contract Timeline.  In the event the successful Offeror fails or refuses to execute a formal written contract with the City of Myrtle Beach in form and content acceptable to the City, within ten (10) City business days after notice of acceptance of the proposal, the proposal may be revoked, and all obligations of the City in connection with the proposal may be 	canceled.

12.04	Notification.  Proposal tabulations will be available on-line at

www.cityofmyrtlebeach.com/purchasing.html. Winning Offeror will be notified five (5) City business days after proposal tabulations are posted.

13.0	OFFEROR RESPONSIBILITIES:

13.01	Duration of Proposal.  Proposal prices, terms and conditions shall be firm for a period of at least one hundred twenty (120) calendar days from the deadline for receipt of submittal, or until such time as established in the proposal.  The successful proposal shall not be subject to future price escalation or changes of terms if accepted during the one hundred twenty (120) day period, or the specified proposal time.  Price decreases or changes in terms by others after the acceptance of a proposal will not be considered.

13.02	Transfer of Responsibilities.  The contractor shall not assign or otherwise transfer any of 	its responsibilities or obligations under the contract to any other person or entity without 	prior written consent of the City.

13.03	Subcontractors.  The contractor shall be wholly responsible for the performance of all subcontractors and for their acts and omissions, and those of persons either directly or indirectly employed by the contractor, and the fact that subcontractors are subject to the approval of the City of Myrtle Beach shall not affect the contractor’s responsibility in this regard.  The Offeror shall bind every subcontractor to all terms and conditions anywhere 	contained in the contract documents as far as applicable to the work of such subcontractor so that the subcontractor assumes toward the contractor and toward the work all the obligations and responsibilities that the contract assumes toward the City as to the

performance of the subcontractor’s portion of the work.

13.04	Coordination and Contact.  The selected Offeror will be required to assume responsibility for coordination, engineering, delivery, installation, and maintenance of all equipment, software and services offered in their proposal, whether they are the manufacturer or producer of them.  Further, the City of Myrtle Beach will consider the selected Offeror to be the sole point of contact with regard to contractual matters, including payment of any and all charges resulting from the lease or purchase of the entire service equipment and software configuration, when applicable.  Only service and equipment offered by Offerors who have installed similar systems of comparable size will be considered.  All service and equipment offered will be in current standard production and of the latest design.

13.05	Liquidated Damages.  If the Offeror fails to deliver the supplies or perform the services within the time specified in the contract, the Offeror shall, in place of actual damages, pay to the City of Myrtle Beach liquidated damages of __________ per calendar day of delay.  If the City terminates the contract, in whole or in part, the contractor is liable for liquidated damages accruing until the City reasonably obtains delivery or performance of similar supplies or services from an alternate offeror.  These liquidated damages are in addition to excess costs of repurchase due to contract termination.  The Offeror will not be charged with liquidated damages when the delay in delivery or performance is documented to be beyond the control and without the fault or negligence

of the Offeror.

14.0	INDEMNITY CLAUSE:

14.01	Hold Harmless.  The contractor agrees to indemnify and save harmless the City of Myrtle 	Beach, its representatives, employees and agents, from all claims, demands, actions, suits and liabilities arising from the contractor’s own fault or negligence or through the negligence or fault of the manufacturer of goods supplied by the contractor.  This obligation shall extend to and include, all litigation costs and reasonable attorney fees incurred by the City in response to such claims, demands, actions or liabilities, provided it is ultimately determined that such claims result from the contractor’s or manufacturer’s fault or negligence.

15.0	FEDERAL AND STATE LAWS:

15.01	Employment Regulations.  Offerors shall comply with all local, state, and federal

directives, orders, and laws as applicable to this proposal and subsequent contract(s)

including, but not limited to Equal Employment Opportunity (EEO), in compliance with executive Order 11246, Minority Business Enterprise (MBE), and Occupational Safety and Health Act (OSHA), as applicable to this contract and Immigration Bill H4400 which states that every contractor doing business with the City of Myrtle Beach for the physical performance of services with the total value of the contract to be performed in a twelve month period exceeding fifteen thousand dollars ($15,000.00) must agree to the following:

- Register and participate in the federal work authorization program to verify the

employment authorization of all new employees; and require agreement from

its sub-contractors to do the same; or

B.  To employ only workers who:

1.  Possess a valid South Carolina Driver’s License or ID issued by the South Carolina Department of Motor Vehicles;

2.  Are eligible to obtain a South Carolina Driver’s License or ID card in 	that they meet the requirements.

3.  Possess a valid Driver’s License or ID card from another state where the requirements are at least as strict as those in South Carolina.

16.0	FINANCIAL ACCOUNTING:

16.01	Representation.  The selected Offeror shall assign a competent account representative 	acceptable to the City of Myrtle Beach who will represent the Offeror in providing contracted services to the City.  If the account representative is removed by the Offeror, the new representative must be acceptable to the City.

16.02	Payment.  Payments shall be made to the contractor within thirty (30) calendar days of receipt of invoice after inspection by and acceptance of the material, goods and/or service by an authorized representative of the City.

17.0	PROPOSAL REJECTION/WITHDRAWAL:

17.01	Reasons for Rejection.  The City of Myrtle Beach may reject a proposal if:

A.  The Offeror misstates or conceals any material fact in the proposal; or if,

B.  The proposal does not strictly conform to the law or requirements of the

proposal; or if,

C. The proposal is conditional, except that the Offeror may qualify his/her

proposal for acceptance by the City on an “all or none” basis, or a “low item” basis.  An “all or none” basis proposal must include all items upon which proposals are invited.

17.02	Best Interest of City of Myrtle Beach.  The City may, however, reject all proposals whenever it is deemed in the best interest of the City to do so, and may reject any part of a proposal unless the proposal has been qualified as provided in statement.  The City may also waive any minor informalities or irregularities in any proposal.

17.03	Withdrawal Timeline.  Proposals may be withdrawn on a written request, received from Offerors prior to the proposal closing date and time.  Negligence on the part of the Offeror 	in preparing the proposal creates no right for withdrawal of the proposal after the proposal 	has been opened.  No modifications, clarifications, or explanations of any proposals will be allowed after the date and time of closing.

18.0	PROTESTS:

18.01	Procedures/Timelines.  Protest of Proposal Specifications and/or Contract Terms:

- Specifications and contract terms shall be made available for inspection and

copying.  Unless a different deadline is specified in the RFP, protests of the

proposal specifications or contract terms shall be presented to the City in

writing within five (5) City of Myrtle Beach business days prior to proposal

closing.

- Such protest or request for change shall include the reasons for protest or

request, and any proposed changes to specifications or terms.

- Envelopes containing protests of specifications shall be marked and mailed, or

hand delivered within five (5) city of Myrtle Beach business days to the

procurement buyer.

- No protest against award because of the content of proposal specifications or

contract terms shall be considered after the deadline established for submitting

such protest in paragraph A above.

- Submission of a proposal without the timely submission of protest of

specifications or contract terms is deemed a waiver to the right to protest

specifications or contract terms.

- A decision by the procurement buyer shall be given in writing in each of such

cases at least one (1) City of Myrtle Beach business day before the time set for

the opening of proposals.  A copy of the decision may be obtained at the

procurement manager’s office.

- If, in the judgment of the procurement manager, the previously mentioned

inquiry requires explanation or interpretation, any such explanation or

interpretation of said plans, specifications, or other contract documents will be

made by written addendum duly issued with copies mailed or delivered to each

person or firm receiving a set of contract documents.

18.02	Procedures/Timelines.  Intent to Award:

A. The written purchase order shall constitute a final decision of the City of Myrtle Beach to award the contract if no written protest is filed with the City within five (5) City of Myrtle Beach business days of the posting of the proposal tab.  If a protest is timely filed, the purchase order is a final decision of the City only upon issuance of a written decision denying the protest and affirming the award.

B.  Purchasing buyer shall notify winning Offeror five (5) City days after proposal tab is posted on the City website.  It is the responsibility of the Offeror to check the website.  Any actual Offeror who is adversely affected or aggrieved by the award of the contract to another Offeror on the same solicitation shall have five (5) City business days after the posting of proposal tab to submit to the City a written protest of the award.  The written protest shall specify the grounds upon which the protest is based.  The City shall not entertain a protest

submitted after the time period established in this rule or such different period as may be provided in the City’s request for proposals.

C.  Offerors must submit written protests of the intent to award to the procurement manager within five (5) business days.  The written protest must include name and contact information of the protestor, solicitation, title and number, the grounds upon which the protest is based, and relief expected.

19.0	CITY RESERVED RIGHTS:

19.01	Reserved Rights.  The City of Myrtle Beach expressly reserves the following rights:

A.  To reject any and/or all irregularities in the proposals submitted

B.  To reject any and all proposals, or parts thereof, as deemed in the best interest of the City.

C.  To base awards due with regard on quality of services, experiences, compliance with specifications, and other such factors as may be necessary in the circumstances.

D.  To make the award to any Offeror who, in the opinion of senior management, 	is in the best interest of the City.

E.  To make award based on negotiations conducted in accordance with this

solicitation or on the basis of a best and final offer by the Offeror.

F.  Only the evaluation factors specified in this solicitation may be used as a basis 	for award.

19.02	Final Judgment.  If any doubt or difference of opinion arises between the City of Myrtle 	Beach and the Offeror as to the interpretation of this request for proposal, the decision of the City will be final and binding upon all parties.

19.03	Clarification.  The City of Myrtle Beach reserves the right to obtain clarification on any 	point in the Offeror’s proposal. The failure of the Offeror to make additional information available could result in the rejection of the response.  Such clarification might involve the delivery of demonstration equipment to the City for evaluation purposes.  Such hardware 	will be provided at no cost to the City.  The City is not obliged to evaluate any or all products.

19.04	Price Increase.  The City of Myrtle Beach reserves the right to accept or reject any price increase(s) and to cancel any and all item(s) under the contract for which price increase(s) is/are considered unacceptable.

19.05	Loss/Damage.  The City of Myrtle Beach will not be responsible for the loss or damage of any items during the RFP process.

19.06	Performance Failure.  In the event that the Offeror fails to perform any material

obligations, the City of Myrtle Beach reserves the right to give the Offeror written cure notice of such failure.  The Offeror will then have five (5) calendar days to resolve the failure. If the failure is not resolved within five (5) calendar days, the City reserves the right to withhold all money that is due and payable to the Offeror.  Such a remedy is in addition to other remedies that might be available to the City. Moreover, the City reserves the right to terminate the contract if the Offeror exceeds the five (5) calendar days of non-performance without the approval of the purchasing manager.

19.07	Negotiation.  After determining the lowest responsive Offeror(s), but prior to the notice of award to any offeror, the City of Myrtle Beach may elect to open negotiations with the selected responsive and responsible Offeror(s) in an effort to improve the proposal for a period of five (5) days.  In these negotiations, the City may address scope of work, unit pricing, or any other contractual requirements fairly contained within the proposal documents.  In the event that the apparent responsive and responsible low Offeror(s) should decline to negotiate, or should negotiations commence but fail, the City shall reject all or all proposals.

20.0	ADA COMPLIANCE:

20.01	Contact Information.  Questions concerning the proposal requirements or specifications 	should be directed in writing to the procurement buyer shown on the front page of this proposal package.  If you need disability-related accommodations, please 	contact (843) 918-2170.

21.0	SIGNATURES:

21.01	Accuracy and Completeness.  The authorized signer of the proposal shall represent and warrant that they have been sufficiently informed in all matters relating to the specified products; that they have checked their proposal for errors and omissions; that the prices stated in their proposal are correct and as intended are a complete and correct statement of prices.

21.02	Compliance.  By Signature below the Offeror affirms that they have examined,

understands and accepts all instructions, specifications and conditions, and will provide for appropriate insurance, deposits, and performance bonds if required, and will comply fully with specifications as attached for the agreed contract, especially where materials and work are involved, and that any and all registration requirements where required for Offerors as 	set forth in law are met.

______________________________________________________________________________

Signature of Offeror									Date of Signing

______________________________________________________________________________

Print Name of Offeror

If more convenient, tabulations are available for pick-up after final award. No proposal tabulations will be faxed.

General Information for

Fire Alarm System, Sprinkler Maintenance

Fire Extinguisher and Exhaust Hood Cleaning Maintenance

PURPOSE

The purpose of this Request for Proposal is to acquire Fire Alarm System, Sprinkler Services, Fire Extinguisher, and Exhaust Hood Cleaning Maintenance and repairs under one (1) contractor for Myrtle Beach Convention Center.

It is the intent of this proposal to establish a term contract for Fire Alarm System, Sprinkler Services, Fire Extinguisher, and Exhaust Hood Cleaning Maintenance for Myrtle Beach Convention Center, located 2101 North Oak Street, Myrtle Beach, SC.

Servicing shall include Fire Alarm System (annually), Sprinkler/pump system (annually), Fire extinguisher (annually) and Exhaust hood cleaning (semi-annually) performing, as required, annual maintenance, recharging, six (6) year maintenance and hydrostatic testing.

The successful Contractor shall be responsible for providing all materials, supplies, parts, tools, equipment, labor, supervision and transportation necessary to perform the work required under this contract.

The successful Contractor shall also have the capability of providing for purchase, if needed, various types and sizes of portable fire extinguishers and universal wall mounting brackets.

The potential contractor will be required to be a certified contractor for Fire Alarm Control Panel, Sprinkler/pump system, Fire extinguishers and Exhaust hood cleaning and inspections. Contractors will be allowed to summit sub-contract pricing for any of the services for which they do not specifically provide. For bid purposes only, each individual part of the contract are to be priced separately.  The awarded contractor will submit invoicing for all services. Due to the busy schedule of the Convention Center, it is the intent to have all services performed at the same time, based on frequency. Contractor will provide a single point of contact for all scheduling of services. This contact will oversee all services, including sub-contractors, and will coordinate with the Convention Center Facility Engineer, Zeke Fowler (843) 918-1258.

Offeror, at its own expense and at all times, shall take all reasonable precautions to protect persons and the Convention City property from damage, loss or injury resulting from the activities of Offeror, its employees, its subcontractors, and/or other persons present.  Offeror will comply with all specific job safety requirements promulgated by any governmental authority, including without limitation, the requirements of the Occupational Safety Health Act of 1970.

General Information

EVALUATION: The evaluation criteria are listed in order of importance:

- Cost; Unit and Total. 40%

- Responsiveness of the proposal, i.e., completeness and clarity. 30%

- The exhibited expertise/experience of the offering firm staff in working with the government offices to the product and/or services being offered.

Relative accessibility of offering firm’s staff and/or services for the convenience. 30%

One (1) original and two (2) copies of your offer should be submitted.  The City will not assume responsibility for any costs related to the preparation or submission of the offer.

The Contractor shall also perform routine/emergency repairs on an “as needed basis”.

TERM OF CONTRACT AND RENEWAL OPTION

The term of the contract shall be for a period of five (5) years with a base year and an option to renew for four (4) additional one (1) year periods provided both parties agree and the terms and conditions remain the same.

PROPOSAL PRICES

Bid prices shall remain firm for the entire term of the contract. A price increase will be allowed at the beginning of the contract renewal period, should the contract be renewed, however, the price increase shall not exceed the percentage of increase established as a result of this bid.

The City will award to one (1) contractor for services of fire alarm system, sprinkler/pump system, fire extinguisher, and exhaust hood cleaning for the term contract.  The award will be made in the best interest of the City.

REPAIR SERVICE

Repairs may not exceed five thousand dollars ($5000.00) per job. Repairs expected to exceed $5000.00 per job shall be bid separately from this contract.

#### PER-BID MANDATORY CONFERENCE

An on-site pre-bid conference will be mandatory for the Convention Center that has the type(s) of fire protection system(s) being bid to ensure that all bidders have thoroughly familiarized themselves with the types(s) of system(s), conditions, nature and extent of work required. All contractors are to meet at the front lobby next to the escalators.

LICENSES, PERMITS, REGISTRATIONS AND CERTIFICATIONS

Each firm bidding for inspection, testing and repair service for the Fire Alarm and Detection Systems, Sprinkler/pump system, fire extinguisher and Exhaust hood cleaning and inspection are specified herein shall be a certified licensed for all services provided issued by the South Carolina Department of Labor, License and Regulation (LLR) Contractor Licensing Board and shall employ on a full time basis one or more employees who hold National Institute for the Certification of Engineering Technologies (NICET) Level II Technician certifications.

All contractor employees performing work under this contract must be thoroughly trained and experienced service technicians certified to inspect, test and repair the specified systems.

Copies of bidding firm’s Contractor’s license(s) and employee licenses, permits or certifications must be submitted with the bid package or the bid may not be considered.

After award, should any Contractor or Contractor employee license, permit or certification be suspended or revoked, notice must be given to the City within five (5) working days.

City of Myrtle Beach Business License

Upon award of the contract, the successful Contractor shall have or must obtain a valid and current City of Myrtle Beach Business License prior to conducting any work under the contract. For questions regarding a business license, please contact the City of Myrtle Beach Business License Division at 843-918-1200.

Additional Licenses, Permits, Registrations and Certifications

The Contractor and all contractor employees to perform work under this contract must possess any/all other applicable licenses, registrations and/or certifications required to perform the specified services. No license, registration or certification shall be applied for in the name of, or on behalf of, the City of Myrtle Beach.

The Contractor shall bear the cost of securing all required licenses, permits, registrations and certifications and for the payment of any/all applicable fees and/or taxes required to perform the services under the contract.

REGULATIONS, STANDARDS, CODES AND ORDINANCES

The successful Contractor shall ensure compliance with all applicable federal, state, county, municipal and local statutes, regulations, standards, codes, and ordinances while performing the services required under this contract including, but not limited to ANSI and OSHA standards, International Fire Code, Standard Fire Prevention Code, NFPA Standard 72-National Fire Alarm and Signaling Code,  NFPA 25 -Standard for the Inspection, Testing and Maintenance of Water-Based Fire Protection Systems, NFPA 1962-Standard for the Inspection, Care, and Use of Fire Hose, Couplings and Nozzles and the Service Testing of Fire Hose and NFPA 70-National

Electrical Code,. The latest edition(s) or when applicable, edition(s) as adopted by the local authority having jurisdiction shall apply.

It shall be the responsibility of the Contractor to remain fully informed of existing and future federal, state, county, municipal and local statutes, regulations, standards, codes and ordinances pertaining to the services to be performed under this contract. Ignorance on the part of the Contractor shall not, in any way, relieve the Contractor from responsibility for compliance with said statutes, regulations, standards, codes and ordinances.

PAYMENT OF FINES AND PENALTIES

The Contractor shall pay all fines and/or penalties assessed the City by any law organization or entity having jurisdiction for the Contractor’s violations of applicable statutes, regulations, standards, codes, ordinances and/or orders arising in connection with the Contractor’s performance of services under the contract.

DRUG FREE WORKPLACE

The Contractor shall maintain a drug free workplace throughout the entire term of the contract.

A “drug free workplace” means a site for the performance of work done in connection with a specific contract of an entity at which employees of the entity are prohibited from engaging in the unlawful manufacture, distribution, dispensation, possession or use of a controlled substance.

ATTIRE

All contractor employees shall wear company uniforms or other appropriate attire while performing the services required under the contract. Shirts and shoes must be worn at all times while performing work for the City.

SERVICE CALL TELEPHONE NUMBER

The Contractor must maintain at all times during the term of this contract, and shall furnish to the Convention Center included in the contract, a central service call telephone number that can be reached twenty-four (24) hours a day, seven (7) days a week for repair service. It shall be the Contractor’s responsibility to notify the Convention Center if/when the service call telephone number is changed, out of order, temporarily disconnected, etc.

##### COMPENSATION AND PAYMENT

Services performed for the Convention Center shall be invoiced and shall be submitted for payment upon satisfactory completion of each service. No invoices shall be submitted prior to services being performed.

All invoices shall include the blanket purchase order number, the name of the facility serviced, an itemized list of services performed, cost for each service, and when applicable, total number of labor hours to perform each service, cost of labor hours per service performed and an itemized list of parts and unit cost per part.

Invoices shall be submitted to:

City of Myrtle Beach

Myrtle Beach Convention Center

2101 North Oak Street

Myrtle Beach, SC 29577

WORKING HOURS

Working hours shall be defined as follows:

Normal Business Hours – 8:00 AM through 5:00 PM, Monday through Friday

Emergency Business Hours – Weekday hours after 5:00 PM, all day Saturday and Sunday and all City holidays.

REPAIR ITEMS IDENTIFIED DURING INSPECTION AND TESTING

Repairs required that are identified during inspection and testing are to be completed only upon approval of the City facility management staff or their authorized representative. The City shall not be responsible for the cost of any repair not properly approved in advance and the City reserves the right to approve or disapprove any repair.

The Contractor shall designate each repair item discovered as routine or emergency on the inspection and testing form to aid the City facility management staff in determining which repair item(s) take priority in being repaired. Routine repair shall be defined as any single work item that does not constitute an emergency, but should be repaired as soon as possible to eliminate inconvenience to occupants or prevent damage to the facility. Emergency repair shall be defined as any single work item that poses an immediate safety hazard, reduces operational effectiveness, or may result in damage to the facility.

When an emergency repair is required, the Contractor, upon discovery, shall verbally advise the City facility management staff or their authorized representative of the nature and location of the needed repair. This verbal notification shall not relieve the Contractor of the requirement to include the emergency repair item in the inspection and testing report.

When an emergency repair is authorized and performed during normal business hours, the repair shall be charged at the routine service call hourly labor rate. If/when it has been authorized for the repair to be performed outside normal business hours, the emergency service call hourly labor rate shall apply.

The City may, at the City’s option, request a written quote for any needed repair prior to approving the repair. When requested, the written quote shall be provided to the requesting facility no later than two (2) working days from date of request. The quote shall include: 1) estimated labor hours to complete repair, 2) itemized list of parts required and cost of each, 4) estimated total cost to complete repair. It shall be the Contractor’s responsibility to ensure that the Contractor has all information necessary to prepare as accurate a quote as possible. Upon authorization to complete a repair when a written quote has been provided, actual cost of the work shall not exceed the quoted price without prior approval of the City facility management staff or their authorized representative.

Repair costs for damage caused by the Contractor or Contractor’s employees shall be the responsibility of the Contractor and shall not be billable to the City.

ROUTINE/EMERGENCY REPAIR SERVICE ON “AS NEEDED” BASIS

The Contractor shall also perform routine/emergency repair services on an “as needed” basis.

Work required that does not constitute an emergency, but should be repaired as soon as possible to eliminate inconvenience to occupants or prevent damage to the facility shall be defined as a routine repair. Work required that poses an immediate safety hazard, reduces operational effectiveness, or may result in damage to the facility shall be defined as an emergency repair.

The Contractor shall contact a City facility requesting routine repair service within twenty-four (24) hours after receiving notification of the need for repair. Unless instructed otherwise by an authorized City representative, routine repairs shall be completed during normal business hours, as soon as possible after notification of the need for repair services.

The Contractor shall immediately contact a City facility requesting emergency repair service and unless otherwise instructed by City personnel, shall respond on-site within two (2) hours after receiving notification of the need for repair. City personnel may, when requested by the Contractor, assist the Contractor in trying to determine/solve the problem over the telephone, however the City shall bear the sole responsibility in determining what constitutes an emergency and the Contractor shall respond on-site upon the City’s request.

#### When emergency repairs are completed during normal business hours, the repairs shall be billed at the routine repair service hourly labor rate, unless the two (2) hour on-site response time is required and met, in which case the emergency repair service hourly labor rate will apply.

#### Time charged for routine/emergency repair service calls shall begin upon arrival and beginning work at the job site and shall end upon completion of work and departure from the job site. City facility staff shall be notified of the arrival and departure times of the Contractor.

All costs, including but not limited to, truck charges, travel time, per diem, mileage, fuel and labor shall be included in the routine/ emergency repair service hourly labor rate bid prices. The cost for parts, if required, will be the only charge allowed to be billed separately.

#### PARTS

The Contractor shall maintain an adequate stock of commonly used replacement parts to ensure that repairs can be completed in a timely manner. All replacement parts used shall be original equipment manufacturer (OEM) parts or approved equals. An approved equal shall meet or exceed the OEM’s specifications for the part being replaced.

All electrical parts provided by the Contractor shall be Underwriters Laboratory (UL) listed and comply with all UL standards in cases where UL has published lists and standards applicable for the item required and the application for which its use has been assigned.

The City understands that the Contractor may not supply all parts for all systems currently installed throughout the City. As such, at a minimum, the Contractor must commit to providing all effort necessary in obtaining needed parts for the City.

The City shall use its discretion in obtaining parts. When upon performing an inspection, testing or repair it is determined that replacement parts are needed, the Contractor shall provide an itemized list of the required parts to the management staff of the City facility being serviced and shall obtain management approval prior to replacing the parts. When management approval is given to replace parts, upon request by the City, all damaged/defective parts replaced shall be returned to the City for its inspection. Parts shall be labeled, identifying the part(s), the system(s) and the location(s) within the system(s) from which the parts were removed.

All parts sold to the City must be itemized on the invoice showing the actual cost of the parts to the Contractor plus the percentage of markup over cost for the parts. When charging for installation of parts, parts and labor invoices shall be submitted simultaneously. A manufacturer/supplier’s invoice may be requested by the City at any time to substantiate invoice prices for parts.

PARTS WARRANTY

The warranty period for parts furnished shall be for the manufacturer’s standard warranty period. The warranty period shall commence upon date of acceptance by the City. The Contractor shall provide an authorized City representative any written manufacturer warranty documents upon completion of the installation.

SPECIAL REQUIREMENTS

The Contractor shall coordinate all working hours with the Convention Center and the work hours are to be approved by the City. Once work begins, work will be continuous, conducted daily and not delayed for any Contractor reason(s).

It shall be the responsibility of the Contractor to furnish the appropriate service manuals, proper types of tools, equipment and materials required while performing the services under this contract. All materials incorporated in the permanent work shall be new and both workmanship and materials shall be the best of quality.

The Contractor shall guarantee all work performed under this contract against any defects in workmanship and shall satisfactorily correct at no cost to the City any such defect that becomes apparent within a period of one (1) year after completion of work. The warranty period shall commence upon date of acceptance by the City.

All work shall be completed in such a manner as to minimize disruption to the normal operation of the facility employees. Access to building(s) must be maintained at all times.

The Contractor shall be totally responsible for the safety of and associated hazards/liabilities of the work to be conducted. Sound safety practices will be adhered to.

The Contractor shall take proper measures to protect adjacent or adjoining property that might be injured and/or damaged by any process of the work to be done. In case of injury or damage, the Contractor shall restore, to the satisfaction of the City and at the Contractor’s expense, the injured or damaged property to a condition similar or equal to that existing before such injury or damage was done.

The Contractor shall provide any and all barricades and lights required for the work or portion of the work within which operations are being conducted. All operations and stockpiles of material and/or stored equipment shall be adequately barricaded and lighted.

Upon completion of the work, the Contractor shall be responsible for cleaning and removing from the job site all debris, materials and equipment associated with the work being performed. The entire work area shall be cleaned to a normal or “first class” condition as judged by the City.

SCOPE OF WORK – Fire Alarm System & Sprinkler/Pump System

REQUIRED WORK

Type(s) of fire protection system(s) located at Convention Center may vary and the specifications provided herein shall pertain only to the type(s) of fire protection system(s) located at each facility.

All fire protection systems shall be inspected and tested according to the equipment manufacturer’s recommended procedures, these bid specifications and the terms and conditions stated herein.

Inspection and testing shall be performed on all fire protection systems at the Convention Center on an annual basis. Inspection and testing shall be performed semiannually on the Convention Center fire alarm and detection system, fire sprinkler system and fire pump system and annually on the Convention Center Class III standpipe system.

- Ensure system is in service prior to inspection and testing.

- Identify and document any potentially detrimental site and environmental condition(s) that could compromise the performance of mechanical and/or electronic components of the system.

- Ensure that the system is adequate and suitable in terms of general occupancy environment, operations and conditions of the facility.

- Ensure that any changes or modifications that have been made to the system are adequate and satisfactory.

- Ensure that storage of combustibles within the facility is proper in relation to the fire alarm and fire detection system.

- Visually inspect and functionally test the condition of all control equipment, including but not limited to control/remote panels, fuses, interfaced equipment, lamps, LEDs and primary power supplies.

  - Control equipment shall be inspected and tested to verify correct receipt of alarm, supervisory, and trouble signals (inputs), operation of evacuation signals and auxiliary functions (outputs), circuit supervision including detection of open circuits and ground faults, and power supply for detection of loss of AC power and disconnection of secondary batteries.

- Inspect and test control unit trouble signals.

  - Operation of panel trouble signals shall be verified for proper operation as well as the ring-back feature for systems using a trouble-silencing switch that requires resetting.

  - Disconnect/isolating switches shall be tested to ensure they are performing as intended.

  - When the system has a ground-fault monitoring circuit, the occurrence of ground fault indications shall be verified whenever any installation conductor is grounded.

  - Transmission of signals to off-premise locations shall be tested.

- An initiating device shall be actuated and receipt of alarm

signal at the off-premises location shall be verified.

- A trouble condition shall be created and receipt of the

trouble signal at the off-premises location shall be verified.

3.  A supervisory device shall be actuated and receipt of the

supervisory signal at the off-premises location shall be verified.

4. When the transmission carrier is capable of operation under

a single or multiple fault condition, an initiating device shall

be activated during such fault condition and receipt of a trouble

signal at the off-premises location shall be verified, in addition

to the alarm signal.

5.   Fiber optic transmission lines shall be tested in accordance with the

manufacturer’s instructions. The relative figure for each line shall

be recorded in the fire alarm control panel.

6.  Each initiating device, indicating appliance and signaling line

circuit shall be tested for correct indication at the control unit.

  - The rating and supervision of fuses shall be verified.

  - The integrity of single or multiple circuits providing interface between two or more controls panels shall be verified. Test interfaced equipment connections by operating or simulating operation of the equipment being supervised. Signals requiring transmission shall be verified at the control panel.

  - Lamps and LEDs shall be illuminated.

  - All secondary (standby power) shall be disconnected and tested under maximum load, including all alarm appliances requiring simultaneous operation. All secondary (standby) power shall be reconnected at end of test. Each redundant power supply shall be tested separately.

- On both the City facility alarm system and monitoring station system visually inspect batteries for corrosion or leakage and ensure that connections are tight.

Check the electrolyte level in lead-acid batteries. Perform appropriate tests such as charger, discharge, load voltage or specific gravity tests on lead-acid, sealed lead-acid or nickel-cadmium batteries. Batteries shall be replaced in accordance with the alarm equipment manufacturer’s recommendations or when the recharged battery voltage/current falls below the manufacturer’s recommendations. All replacements, noting location and reason for replacement shall be included in the inspection and test report.

- Inspect lightning protection equipment such as transient suppressors.

- Inspect and test emergency communications equipment:

  - Amplifier/tone generators shall be tested by verifying correct switching and operation of backup equipment.

  - Call-in signal silence function shall be operated and receipt of correct audible and

visual signals at control panel shall be verified.

  - Off-hook indicator (ring down) shall be tested by installing phone set or removing phone from the hook and verifying receipt of the signal at the control panel.

  - Phone jacks shall be visually inspected and communications path through

jack shall be initiated.

  - All phone sets shall be activated and verified to be operating correctly.

  - System performance shall be tested by operating handsets simultaneously and verifying that voice quality and clarity are good.

- Visually inspect and test all annunciators and zones by tripping detector. Perform lamp test, initiate trouble test to remote trouble indicator and test trouble ring-back. If provided, the correct operation of annunciators shall be tested under fault conditions.

- Visually inspect and functionally test all initiating devices:

  - Restorable and non-restorable-type link electromechanical releasing devices shall be tested for correct operation by removal of the fusible link and operation of the associated devices.

  - Air sampling tests shall be performed, detector alarm response verified through the end sampling port on each pipe run and airflow through all other ports shall be verified.

  - Air duct detectors shall be inspected and tested to ensure that the device will sample the air stream.

  - Heat detectors shall be inspected and tested using test methods appropriate for the type of heat detector to be tested. A test method shall be used that will not damage non-restorable fixed-temperature elements of a combination rate of rise/fixed-temperature element detector. Two or more restorable fixed-temperature, spot-type heat detectors shall be tested on each initiating circuit annually. Different detectors shall be tested each year and each detector shall be tested within a five (5) year period.

  - Radiant energy fire detectors (flame and spark/ember) shall be sensitivity tested to ensure that each detector is operating correctly.

  - Smoke detectors/alarms shall be inspected and tested. Sensitivity tests shall be performed as required using proper test methods. Sensitivity shall not be

tested/measured using any device that administers an unmeasured concentration of smoke or other aerosol into the detector/alarm.

  - Projected beam type detectors shall be tested by introducing smoke, other aerosol or an optical filter into the beam path.

  - Fire alarm boxes (pull stations), both manual and key-operated pre-signal types, shall be tested for proper operation.

  - Water-flow devices and supervisory initiating devices including, but not limited to, control valve, tamper, room/water temperature, water level and low-pressure alarm switches shall be inspected and tested and receipt of signals verified.

- Inspect and functionally test all alarm indicating appliances including supervised, audible (such as bells, horns, chimes), audible textural (appliances that convey voice messages) and visible (such as strobe) devices to ensure they are operating properly. The sound pressure of audible and audible textural devices shall be measured and recorded. Audible information shall be verified to be distinguishable and understandable. Visible appliances shall be inspected to ensure that they are in the proper locations and functionally tested to ensure that each appliance flashes properly.

- Inspect and perform tests on supervising station fire alarm system transmitters and supervising station fire alarm system receivers.  Tests shall be performed on all system functions and features to ensure correct operation. Initiating devices shall be activated and receipt of the correct initiating device signal shall be verified at the supervising station. Upon completion of the tests the system shall be restored to its functional operating condition. When test jacks are used, the first and last tests shall be made without the use of the test jack. Other tests that are required and are specific to the type of transmitter/receiver being tested shall also be performed.

- Test door holders ensuring door release devices including closers and latches are operating normally.

- Test elevator recall relay ensuring relays to primary and alternate floors are operating normally and elevator restarts from fire shutdown service automatically.

- Test HVAC shutdown outputs to ensure air handler shutdown is normal and air handler(s) restart from shutdown automatically.

- When authorized to do so, complete any necessary repairs and replace parts as required.

- Ensure alarm panels are cleared and system is returned to normal operation.

Complete results of the inspection and testing shall be recorded on an NFPA acceptable Inspection and Testing Form. The form shall include for all accessible equipment, devices, appliances and components the type of inspection/testing performed (visual/functional/both), applicable voltages, locations of each initiating device and indicating appliance tested including system address or zone location and the test results. When the operation of a device, circuit or control panel function is simulated, documentation shall reflect that the operation was simulated and shall indicate by whom it was simulated. Any/all problems found and the corrective action taken or recommended in accordance with recognized procedures for care and maintenance shall be fully explained on the form. The form shall also contain the name of the company, name of company employee performing the services and signature of an authorized City facility representative acknowledging satisfactory completion of the services.

The Contractor shall be responsible for placing one (1) copy of the inspection and testing report beside the fire alarm system panel, providing one (1) duplicate copy to the City facility management staff and forwarding one (1) duplicate copy of the report to the City of Myrtle Beach Fire Marshall, PO Box 2468, Myrtle Beach, SC 29578-2468.

SCOPE OF WORK – Sprinkler/Pump System

REQUIRED WORK

Inspection and testing shall be performed on all fire sprinkler system equipment and components thereof, including, but not limited to, sprinkler heads, piping, hangers/braces, valves, gauges, fire department connections and supervisory and water flow devices. All equipment, devices and components shall be inspected and tested to ensure that all electronic and mechanical components are in good repair and functioning properly.

Fire sprinkler system inspection and testing service shall include, but is not limited to the following actions (as applicable to the system being inspected and tested):

- Prior to inspection and testing, notify the City facility management staff or their authorized representative, building occupants and the monitoring facility that receives alarm, supervisory or trouble signals to prevent unnecessary response during testing period. Upon completion of testing, notify all appropriate personnel that testing has been completed.

- Ensure that system is in service prior to inspection and testing.

- Identify and document any potentially detrimental site/environmental condition(s)/clearance issue(s) that could compromise the performance of mechanical and/or electronic components of the system.

- Inquire about changes in building status that may affect the performance or reliability of the system.

- Ensure that any changes or modifications that have been made to the sprinkler system are adequate and satisfactory.

- Ensure that storage of combustibles within the facility is proper in relation to the fire sprinkler system.

7.   Inspect building to ensure that system is adequately protected against freezing weather.

- Inspect all accessible sprinkler heads for adequate clearance and condition to allow for proper spray pattern activation and distribution. Sprinklers shall be checked for proper type and temperature rating, proper installation, obstructions, physical damage/leakage, corrosion, loading, foreign materials and paint. Testing shall be performed when required.

- Check supply of spare sprinkler heads for proper types and quantities and ensure wrench for each type sprinkler head is on hand.

- Inspect the condition of visible and accessible sprinkler pipes and fittings to ensure that they are in good condition, free from mechanical damage, leakage, corrosion, misalignment and have no external loads of materials resting or hung from the pipes.

- Inspect hangers and seismic braces to ensure that they are not damaged or loose.

- Inspect hydraulic nameplate to ensure that it is legible and securely attached to the sprinkler riser.

- Inspect post indicator valves to ensure they are in good condition and test by opening valve until spring or torsion is felt in the rod to ensure that rod has not become detached from the valve. Valve shall be backed one-quarter turn from the fully open position to prevent jamming.

- Inspect control valves to ensure that they are accessible, in good condition, in the normal open or closed position, properly sealed, locked or supervised, free from external leaks, and are marked with appropriate signage identifying the system or portion of the system that the valve controls. Each control valve shall be operated through its full range and returned to its normal position. Yoke valves shall be completely closed and reopened to test valve operation. OS&Y valves shall be backed one-quarter turn from the fully open position to prevent jamming.

- Inspect alarm valves externally to ensure valves are in good condition and have no physical damage, are in the appropriate open or closed position, gauges indicate normal supply water pressure is being maintained and the retarding chamber or alarm drains are not leaking. Unless tests indicate a greater frequency is necessary, valves shall be inspected internally every five (5) years to ensure all internal parts (strainers, filters and restriction orifices) operate correctly, move freely and are in good condition.

- Inspect check valves to ensure that they are in good condition and are not leaking. Check valves shall be inspected internally every five (5) years to ensure that all internal components operate correctly, move freely and are in good condition.

- Inspect pressure reducing/pressure relief control valves to ensure that valves are in good condition, handwheels are not broken or missing, valves are in the open position, are not leaking and are maintaining downstream/upstream pressures per design criteria. Perform partial flow tests annually to move the valves from their seats. Full flow tests shall be performed every five (5) years, compared to previous test results and adjustments made if necessary.

- Inspect drain valves and related equipment.

- Inspect system gauges to ensure that they are in good condition and normal pressure is being maintained. Gauges shall be replaced every five (5) years or tested every five (5) years by comparison with a calibrated gauge.

- Inspect and test valve supervisory switches to ensure a distinctive signal indicates movement from the valve’s normal position or when the stem of the valve has moved from its normal position. The signal shall be restored only at the normal position.

- Inspect and test water-flow alarm devices including, but not limited to mechanical water motor gongs, pressure switch and vane-types to ensure they are in good repair and operating correctly.

- Check fire department hose connections to ensure that they are visible and accessible, caps/plugs are in place and are not damaged, couplings/swivels are not damaged and rotate smoothly, threads are in good condition, gaskets are in place and in good condition, check valve is tight and is not leaking, automatic drain valve and clappers are in place and operating properly and identification signs are in place. When caps/plugs are missing, the interior of the connection shall be inspected for obstructions and the clapper shall be checked to ensure it is operational over its full range.

- Inspect and test dry pipe portions of the system (where applicable):

- Inspect valve enclosures and heating equipment to ensure that they are in

satisfactory condition. If installed in valve enclosures, low temperature

alarms shall be inspected and tested at the beginning of the heating season.

- Inspect gauges to ensure that the gauges on the supply side of the dry pipe

valves indicate normal supply water pressures are being maintained  and

gauges on the system side of the valves indicate that the proper ratio of

air/nitrogen pressure to water supply pressure is being maintained. Gauges

on quick-opening devices shall indicate the same pressure as gauges on the

system side of the valve.

c.  Inspect low air/nitrogen pressure alarms.

d.  Inspect dry pipe valves externally to ensure they are free of physical

damage, trim valves are in appropriate open or closed position and

intermediate chambers are not leaking. Strainers, filters and restricted

orifices shall be inspected internally every five (5) years unless tests indicate

a greater frequency is necessary.

e.  Test priming water level to ensure it returns to normal.

f.   Perform trip tests on dry pipe valves with the control valve partially open and

compare with previous trip test results. Every three (3) years the dry pipe valve

shall be trip tested with the control valve fully open and the quick-opening device,

if provided, in service.

g.  Test automatic air pressure maintenance devices during the dry pipe valve trip test.

h.  Test quick-opening devices.

i.   Drain low points after each operation and before the onset of freezing weather

conditions.

j.  Complete and attach tag to valve showing date of trip test, company name and name                    of company employee performing the test.

24. Conduct main drain tests at each riser to determine whether there has been a change in condition of the water supply piping and control valves. Ensure adequate drainage is provided prior to performing tests.

25. Tag devices when required.

26. When authorized to do so, complete any necessary repairs and replace parts as required.

27. Ensure alarm panels are cleared and system is returned to normal operation.

Complete results of the inspection and testing performed shall be recorded on an NFPA acceptable Inspection and Testing Form. Information to be documented shall include, but is not limited to, type of device inspected/tested, location of device, type of inspection/testing performed (visual/functional/both) and applicable flow rates/pressure readings. Any/all problems

found and the corrective action taken or recommended in accordance with recognized procedures for care and maintenance shall be fully explained on the form. The form shall also contain the name of the company, name of the company employee performing the services and the signature of an authorized City facility representative acknowledging satisfactory completion of the services.

The Contractor shall be responsible for placing one (1) copy of the inspection and testing report beside the system control valve, providing one (1) duplicate copy to the City facility management staff and forwarding one (1) duplicate copy of the report to the City of Myrtle Beach Fire Marshall, PO Box 2468, Myrtle Beach, SC 29578-2468.

Fire Pump Systems

Inspection and testing shall be performed on all fire pump system equipment and components thereof, including but not limited to, fire pump assemblies, drivers, controllers, fuses, circuit breakers and alarms. All equipment, devices and components shall be inspected and tested to ensure that all electronic and mechanical components are in good repair and functioning properly.

Fire pump system inspection and testing shall include, but is not limited to, the following actions (as applicable to the system being inspected and tested):

- Prior to inspection and testing, notify the City facility management staff or their authorized representative, building occupants and the monitoring facility that receives alarm, supervisory or trouble signals to prevent unnecessary response during testing period. Upon completion of testing, notify all appropriate personnel that testing has been completed.

- Ensure that system is in service prior to inspection and testing.

3.   Identify and document any potentially detrimental site/environmental condition(s)

or clearance issue(s) that could compromise the performance of mechanical and/or

electronic components of the system.

4.   Inquire about changes in building status that may affect the performance or

reliability of the system.

5.   Ensure that any changes or modifications that have been made to the system are

adequate and satisfactory.

6.   Ensure that storage of combustibles within the facility is proper in relation to the

fire pump system.

7.   Ensure pump house heating is adequate and ventilating louvers operate freely when

fire pump system is housed in pump house.

- a. Check pump system conditions to ensure control valves are accessible, in good

condition, in the normal open or closed position, properly sealed, locked or

supervised and free from external leaks. Ensure pump suction, discharge and

bypass valves are fully open, piping is free from leaks and corrosion,

suction/system line pressure gauge readings are normal, suction reservoir is full

and wet pit suction screens are in place and unobstructed.  Check pump packing

glands for discharge. Check for unusual noise or vibrations. Check packing boxes,

bearings, or pump casing for overheating and record pump starting pressure. Check

pump shaft end play and  pump coupling alignment.

b. Check pump electrical system conditions to ensure controller pilot light (power

on), transfer switch normal pilot light and isolating switch (standby emergency

source) are illuminated, reverse phase alarm pilot light is off or normal phase

rotation pilot light is on and oil level in vertical motor sight glass is normal. Test

isolating switch and trip circuit breaker. Operate manual starting means

(electrical) and inspect and operate emergency manual starting means (without

power). Check electrical connections and inspect wiring for chafing. Check pressure

switch settings for proper calibration. Observe the time for motor to accelerate to

full speed, record the time controller is on first step (for reduced voltage or reduced

current starting) and record the time pump runs after starting (for automatic stop

controllers).

c. Inspect pump system mechanical transmission.

9.  Check diesel engine system conditions:

a. Ensure controller selector switch is in auto position, battery voltage and charging

current readings are normal, battery pilot lights are on or battery failure pilot lights

are off,  all alarm pilot lights are off and engine running time meter is reading,

observe the time for engine to crank, time for engine to reach running speed, engine

oil pressure gauge, speed indicator and water and oil temperature indicators while

engine is running and record abnormalities

b.  Diesel engine fuel system: Check fuel tank level to ensure it is two thirds full,

inspect and test tank float switch, inspect and test solenoid valve operation,

ensure strainer, filter or dirt leg or combination thereof are clean, ensure there is

no water or foreign material in tank, visually inspect flexible hose and connectors,

visually inspect piping and inspect and test tank vents and overflow piping to

ensure they are unobstructed.

c.  Diesel engine lubrication system: Check oil level and oil filter, check right angle

gear drive oil level, check lube oil heater, check crankcase oil level and ensure

crankcase breather is clean.

d.  Diesel engine cooling system: Check cooling system level, test antifreeze

protection level, check and ensure there is adequate cooling water to heat exchanger,

visually inspect water pumps, visually inspect and check condition of flexible hoses

and connections, check water jacket heater to ensure it is operating properly, inspect

combustion air duct work, louvers and water strainer.

e.  Diesel engine exhaust system: Check for leakage, check drain condensate trap,

visually inspect for insulation and fire hazards, test for excessive back pressure,

visually inspect exhaust system hangers and supports and visually inspect

flexible exhaust section.

f.  Diesel engine battery system: Check electrolyte level, inspect terminals and exterior

casing to ensure they are free from corrosion, ensure terminal connections are tight,

test specific gravity or state of charge, inspect charger and charge rate and check

equalize charge.

g.  Diesel engine electrical system: Check control and power wiring connections to

ensure they are tight, visually inspect for wiring chafing, test operation of safety

devices and alarms and inspect circuit breakers or fuses.

- Check steam system conditions to ensure steam pressure gauge reading is normal. Record steam pressure gauge reading and observe time for turbine to reach running speed.

- Using proper test method(s), test pump assembly under minimum, rated and peak flows of the fire pump by using pump suction pressures, discharge pressures and flowmeter measurements to determine total pump output.. All water spills shall be mopped dry after testing is complete.

- Conduct visual observations, measurements and adjustments while the pump is running and flowing water during the following output conditions:

a. No-flow condition (churn) - Check circulation relief valve for operation to discharge

water. When pressure relief valve is installed, observe the valve closely during each

flow condition to determine if the pump discharge pressure exceeds the normal

operating pressure of the system components and if the valve closes at the proper

pressure. Close the valve during flow conditions if necessary to achieve minimum

rated characteristics for the pump and reset valve to the normal position at the

conclusion of the pump test. Perform test for one-half hour.

b. At each flow condition-record electric motor voltage and current on all lines, record

pump RPM speed and record simultaneous reading of pump suction, discharge

pressure and pump discharge flow.

- Test automatic transfer switch to ensure the overcurrent protective devices, such

as fuses or circuit breakers, do not open by simulating power failure condition

while pump is operating at peak load and verifying that the switch transfers power

to the alternate power source and the pump continues to perform at peak load.

Remove the power failure condition and verify that after a time delay, the pump is

reconnected to the normal power source.

- Simulate alarm conditions by activating alarm circuits at alarm sensor locations

and observe all local/remote alarm indicating devices (audible/visual) for correct

operation.

15. Inspect suction screen for debris or obstructions after the water-flow test or fire

protection system activations are complete.

16. Check parallel and angular alignment of the pump and driver during the testing for any

misalignments.

17. Evaluate pump performance by:

a. Comparing the test results with the initial unadjusted field acceptance test curve

or the performance characteristics indicated on the pump nameplate. Degradation in

excess of five (5) percent of the pressure of the initial  unadjusted acceptance test

curve or nameplate shall be investigated to determine the cause of the degraded

performance.

b. Comparing current and voltage readings to ensure that they do not exceed the

rated voltage and rated full-load current multiplied by the permitted motor service

factor. Voltage reading at the motor within five (5) percent below or ten (10) percent

above the rated (i.e. nameplate) voltage shall be considered acceptable.

18. Ensure all devices are tagged when required.

19. When authorized to do so, complete any necessary repairs and replace parts as required.

20. Ensure alarm panels are cleared and system is returned to normal operation.

Complete results of the inspection and testing performed shall be recorded on an NFPA approved Inspection and Testing Form. The report shall provide comprehensive test results detailing pump performance including a detailed tabulation of the results and a plotted performance curve. All

time delay intervals associated with the pump’s starting, stopping and energy source transfer shall be recorded. Any/all problems found and the corrective action taken or recommended in accordance with recognized procedures for care and maintenance shall be fully explained on the form. The form shall also contain the name of the company, name of company employee performing the services and signature of an authorized City facility representative acknowledging satisfactory completion of the services.

The Contractor shall be responsible for placing one (1) copy of the inspection and testing report beside the fire sprinkler/fire pump system control valve, providing one (1) duplicate copy to the City facility management staff and forwarding one (1) duplicate copy of the report to the City of Myrtle Beach Fire Marshall, PO Box 2468, Myrtle Beach, SC 29578-2468.

Class I and Class III Standpipe Systems

Inspection and testing shall be performed on all Class I and Class III standpipe system equipment and components thereof, including, but not limited to, piping, fire hose cabinets/storage devices/rack assemblies, hose connections, fire hose, valves, pressure regulating devices and alarm devices. All equipment, devices and components shall be inspected and tested to ensure that all electronic and mechanical components are in good repair and functioning properly.

Standpipe inspection and testing shall include, but is not limited to, the following actions (as applicable to the system being inspected and tested):

- Prior to inspection and testing, notify the City facility management staff or their authorized representative, building occupants and the monitoring facility that receives alarm, supervisory or trouble signals to prevent unnecessary response during testing period. Upon completion of testing, notify all appropriate personnel that testing has been completed.

- Ensure that system is in service prior to inspection and testing.

- Identify and document any potentially detrimental site/environmental condition(s) or clearance issue(s) that could compromise the performance of mechanical and/or electronic components of the system.

- Inquire about changes in building status that may affect the performance or reliability of the system.

- Ensure that any changes or modifications that have been made to the standpipe system are adequate and satisfactory.

- Ensure that storage of combustibles within the facility is proper in relation to the standpipe system.

- Inspect visible piping to ensure there are no damaged, corroded or leaking pipes and pipe support devices are in place and are not damaged.

- Inspect hose cabinets for corrosion/damage, ensure cabinet doors open fully and easily, door glazing is not cracked or broken, locks function properly on break-glass type cabinets, glass break devices are attached, valves, hose and nozzles are easily accessible and cabinets are visibly unobstructed and properly identified as containing fire equipment.

- Inspect hose storage devices to ensure that they are not obstructed, damaged or difficult to operate, nozzle clips are in place, nozzles are correctly contained and hose racks will swing out at least 90 degrees.

- Inspect hose rack assembly pressure reducing valves to ensure that hand wheels are not broken or missing and no leaks are present. A partial flow test adequate to move the valve from its seat shall be performed. A full flow test shall be performed every five (5) years, compared to previous test results.

11. Inspect hose connections to ensure that hose valves operate smoothly and are not leaking,

hose caps are in place and are not damaged, hose threads are not damaged, valve handles

are not missing or broken, gaskets are in place and in good condition, restricting devices

are in place and valves are unobstructed. Hose valves shall be tested annually by opening

and closing the valve.

  - When hose connections are equipped with pressure reducing valves, inspect the valves to ensure the valve handles are not missing or damaged, outlet hose threads are not damaged, no leaks are present and the reducer and cap are in place. A partial flow test shall be performed on pressure reducing valves annually to move the valves from their seats. A full flow test shall be performed every five (5) years and compared to previous test results.

12. Inspect fire hose and components:

a.  Unrack/unreel/unroll hose and physically inspect hose to ensure it is free of debris,

has no evidence of mildew, rot, damage by chemicals, burns, cuts, abrasions or

vermin and has  not been vandalized in any way.

  - Inspect hose liner at each end of hose to ensure there is no physical evidence of liner delamination.

  - Visually inspect hose couplings to ensure that they are in serviceable condition and have no defects that impair operation. Check couplings for internal gaskets, damaged or incompatible threads, corrosion, missing lugs, loose external collars, being out of round, swivels not rotating freely and slippage on the hose.

  - Inspect hose nozzles thoroughly to ensure that they operate smoothly and are in the closed position, there are no obstructions in waterways, there are no missing parts or damage to the tips, threads are in good condition, gaskets are in place and in good condition, adjustments such as pattern selection, etc. are fully operable and shut off valves (if/when applicable) are operating properly.

  - If hose fails physical inspection it shall be taken out of service, repaired and service tested or condemned. A replacement hose must be installed while service testing is performed.

  - Perform service testing of hose five (5) years after installation, every three (3) years thereafter and stencil appropriately, based on date of manufacture and service test pressure.

  - Rerack/rereel/reroll hose so that folds do not occur in the same position in the hose and ensure hose is connected to hose rack nipple or valve.

  - Complete and properly attach service tag near female end of hose. Ensure all required information is listed on tag, such as manufacturer, part number, date put in service, inspection date, test date and test results (when applicable), company name and name of company employee performing inspection/testing.

13. Post indicator, control, alarm and check valves shall be inspected the same as fire

sprinkler system requirement #’s 13, 14, 15, and 16.

14. System gauges, valve supervisory switches, water flow alarm devices and fire department

hose connections shall be inspected the same as fire sprinkler system requirements #’s 19,

20, 21 and 22.

15. Dry pipe portions of the system (if applicable) shall be inspected the same as fire

sprinkler system requirement # 23. a-j.

16. Perform hydrostatic testing on dry portions of wet standpipe every five (5) years.

Hydrostatic pressure shall be tested at requirements in effect at time of installation and

test pressure shall be measured at the low elevation point of the individual system or zone

being tested and the inside standpipe piping shall show no leakage. Test requirements and

performance to be discussed with authority having jurisdiction (AHJ) prior to testing.

17. Conduct main drain tests to determine whether there has been a change in condition of the water supply piping and control valves. Ensure adequate drainage is provided prior to performing tests. Tests shall be conducted at the low point drain for each standpipe or at the main drain test connection where supply main enters building (when provided)

18. Perform flow testing when required. Ensure adequate drainage is available before performing the test. Flow test shall be conducted every five (5) years at requirements in effect at time of installation and performed at the most hydraulically remote hose connection of each zone of an automatic standpipe system or at a point dictated by the authority having jurisdiction (AHJ) to verify the water supply still provides the design pressure at the required flow. The actual test methods and performance criteria shall be discussed in advance with the AHJ.

19. When authorized to do so, complete any necessary repairs and replace any parts required.

20. Ensure alarm panels are cleared and system is returned to normal operation.

Complete results of the inspection and testing performed shall be recorded on an NFPA approved Inspection and Testing Form. Information to be documented shall include, but is not limited to, type of device inspected/tested, location of device, type of inspection/testing performed (visual/functional/both) and applicable flow rates/pressure readings. Any/all problems found and the corrective action taken or recommended in accordance with recognized procedures for care and maintenance shall be fully explained on the form. The form shall also contain the name of

the company, name of the company employee performing the services and the signature of an authorized City facility representative acknowledging satisfactory completion of the services.

The Contractor shall be responsible for placing one (1) copy of the inspection and testing report beside the fire sprinkler system control valve, providing one (1) duplicate copy to the City facility management staff and forwarding one (1) duplicate copy of the report to the City of Myrtle Beach Fire Marshall, PO Box 2468, Myrtle Beach, SC 29578-2468.

SCOPE OF WORK – FIRE EXTINGUISHERS

REQUIRED WORK

The successful Contractor shall assist the Convention Center in maintaining accurate fire extinguisher maintenance and repairs.

The successful Contractor shall also have the capability of providing for purchase, if needed, various types and sizes of portable fire extinguishers and universal wall mounting brackets.

### 1.	SERVICING

For proposal purposes, servicing shall mean that one or more of the following is performed when required:

1.1	Annual Maintenance – Performing annually, a thorough external examination of extinguisher and repairing/replacing parts when required.

1.2	Recharging – Refilling extinguisher with extinguishing agent (to include expellant for certain types of extinguishers) due to leakage, vandalism and/or accidental or purposely discharging of extinguisher.

1.3	Six (6) Year Maintenance – Completely emptying extinguisher, performing thorough examination of extinguisher both internally and externally, repairing/replacing parts as needed and recharging extinguisher.

1.4	Hydrostatic Testing - Completely emptying extinguisher, performing thorough examination of extinguisher both internally and externally, repairing and/or replacing parts as needed, pressure testing by hydrostatic methods and recharging extinguisher.

2.	REQUIRED WORK

The Contractor shall schedule and perform maintenance annually at the Convention Center specified in this bid to ensure that the fire extinguishers are in fully operable condition.

The Contractor shall also service extinguishers on an “as needed” basis, when required, at no additional cost to the Convention Center. Upon receiving a request for service, the Contractor shall confirm receipt of the request within twenty-four (24) hours and shall schedule a time to complete the service.

All extinguishers shall be serviced and maintained in accordance with the manufacturer’s recommended maintenance procedures, these proposal specifications and the terms and conditions contained herein.

Fire extinguishers removed from the Convention Center for both scheduled/unscheduled servicing must be returned within twenty-four (24) hours after removal or the Contractor shall provide loaned extinguishers of types and sizes suitable for the type of hazards being protected and of at least equal rating as the removed extinguishers. Loaned extinguishers shall be provided at no charge to the Convention Center.

After servicing, extinguishers shall be returned to the same location found.

### Should the Convention City accidentally or purposely discharge a loaned extinguisher, the Convention Center shall incur the cost of recharging the loaned extinguisher and the cost incurred shall be the same as the proposal price established as a result of this proposal to recharge an extinguisher of the same type and size as the loaned extinguisher. Cost to repair/replace a fire extinguisher due to discharge or damage resulting from negligence on the part of the Contractor shall be at no cost to the Convention Center.

### 3.	Annual Maintenance

The Contractor shall schedule and perform maintenance on all specified fire extinguishers annually, or as required, when federal, state, municipal and local laws, rules, regulations, standards, codes or ordinances dictate otherwise.

The monthly “Quick Check” inspection as described in NFPA 10 is specifically excluded from this contract.

Annual Maintenance shall include, but is not limited, to the following steps (as applicable):

- Ensure extinguisher is in designated place.

- Ensure access to or visibility of extinguisher is not obstructed.

- Ensure extinguisher is securely hung on the proper type hanger.

- Check unit classification to ensure it is properly identified with the appropriate decal and is proper for hazards in the area in which the extinguisher is located.

- Check date of manufacture and determine if six (6) year maintenance service or hydrostatic testing (as applicable) is required or was performed when required.

- Examine externally the cylinder shell and components for missing or substitute parts, damage, corrosion, dents, burns, repairs or other physical conditions that might impair extinguisher function.

- Examine pressure gauge or safety relief assembly (CO2 extinguisher) to ensure that it is of the proper type, installed correctly, within proper operating range and has no damage, corrosion or obstruction.

- Examine valve assembly and ensure valve stem is not corroded or damaged and that there is no powder or foreign matter in valve opening.

- Examine pull pin and check for freedom of movement by breaking the tamper seal and removing pin.

- Examine handle and operating lever to ensure that they operate correctly, are not damaged or corroded and rivets are secure.

- Examine nozzle/hose assembly, verify that it is of the proper type and size and has no cracks, cuts, abrasions, obstructions or thread damage.

- Remove hose assembly, inspect diffuser holes to ensure that they are not damaged or obstructed, perform conductivity test, replace (if applicable) or reinstall and label hose assembly as passing conductivity test (i.e. 10, 15, 20 lb. CO2 extinguishers). Record all required information in accordance with applicable NFPA standards on a durable service tag and securely affix to hose assembly.

- Examine hose retainer/horn retention band to ensure it is secure and properly retains hose/horn.

- Turn unit and fluff powder in dry chemical extinguisher.

- Weigh extinguisher and verify that the total charged weight is within the indicated allowable tolerance printed on the extinguisher.

- Clean cylinder shell of all dirt or foreign deposits and ensure operating instructions are clean, legible, securely affixed to extinguisher and face outward when extinguisher is returned to the proper location.

- Record all required information in accordance with applicable NFPA standards on a durable service tag and securely affix tag to extinguisher.

#### 4.	Recharging and Six (6) Year Maintenance Service

Recharging

The Contractor shall recharge extinguishers, as needed, due to leakage, vandalism and accidental or purposely discharging of extinguishers.

Recharging costs shall be billed separately only when recharging is required due to leakage, vandalism and/or accidental or purposely discharging of extinguishers by City personnel. Recharging required when completing six (6) year maintenance service or hydrostatic testing shall be included in the bid price for the applicable service and shall not be billed separately as “Recharge”.

On-site recharging shall be provided when requested. On site recharging shall mean recharging is provided in a Contractor owned vehicle approved for servicing fire extinguishers and the vehicle is located on the property of the facility being serviced.

Only refill extinguishing agents listed on the cylinder and/or as recommended by the manufacturer shall be used and the Contractor shall maintain an adequate stock of extinguishing agents to ensure that recharging can be accomplished as required.

Halon extinguishers shall be recharged only when approved by the Convention Center. The Contractor shall notify the authorized City facility representative when a halon extinguisher requires recharging and the representative shall determine whether the extinguisher is to be recharged or replaced. Should the Convention Center elect recharging of a halon extinguisher, all costs to claim and recover the extinguishing agent shall be included in the “Recharge” bid price.

5.	Six (6) Year Maintenance

The Contractor shall perform six (6) year maintenance on extinguishers as required.

Recharging required for completion of six (6) year maintenance service shall be included in the six (6) year maintenance bid price and shall not be billed separately as “Recharge”.

Recharging and six (6) year maintenance shall include, but is not limited to the following steps (as applicable):

- Remove pull pin, expel extinguishing agent and depressurize cylinder.

- Remove nozzle/hose assembly, verify that it is of the proper type and size and examine for any internal blockage, damage or wear.

- Remove hose assembly, inspect diffuser holes to ensure that they are not damaged or obstructed, perform conductivity test, reinstall, and label hose assembly as passing conductivity test (when applicable) (i.e. 10, 15, 20 lb. CO2 extinguishers).

- Remove valve assembly from cylinder.

- Remove siphon tube and retainer nut from valve body, examine and replace if any damage or thread wear is evident.

- Remove neck o-ring from valve, examine for cuts, cracking or deformation, lubricate or replace when required.

- Remove valve stem, spring and valve stem o-ring, examine for cracks, deformation, corrosion or damage, clean valve stem and spring, and clean and lubricate valve stem o-ring or replace parts when required.

- Ensure all extinguishing agent is emptied from cylinder and thoroughly examine cylinder condition both internally and externally.

- Examine and clean valve body internal sealing surfaces and internal threads. Clean and lubricate external threads. Replace valve if there is evidence of thread damage, wear, internal scratches or other structural damage.

- Remove safety relief nut, washer and disc assembly, replace with new assembly, install new washer into valve port followed by a safety relief nut (CO2 extinguisher).

- Ensure pressure gauge is of the proper type and is not corroded, obstructed or physically damaged.

- Examine handle and operating lever to ensure they are not damaged or corroded and rivets are secure.

- Reassemble valve and siphon tube.

- Test operating lever to verify proper movement.

- Fill extinguisher to rated capacity with proper extinguishing agent as specified on the extinguisher.

- Attach verification of service collar indicating month and year service performed.

- Lubricate top of valve stem and screw valve assembly and siphon tube into cylinder.

- Attach recharge adapter, proper pressurization source and pressurize to proper charge pressure.

- Insert pull pin into operating lever, disconnect pressurization source, remove recharge adapter and install tamper seal through pull pin.

- Perform leak test on extinguisher using proper medium.

- Reattach nozzle/horn/hose assembly and secure hose/horn into hose/horn retainer/retention band.

- Weigh extinguisher and verify that it meets the charged weight printed on the extinguisher.

- Clean cylinder shell of all dirt or foreign deposits and ensure operating instructions are clean, legible, securely affixed to extinguisher and face outward when extinguisher is returned to the proper location.

- Record all required information in accordance with NFPA standards on durable service tag and securely affix tag to extinguisher. (In detention facilities, only plastic ties shall be used to affix tag to extinguisher).

#### 6.	Hydrostatic Testing

It shall be the Contractor’s responsibility to ensure hydrostatic testing of extinguishers and applicable hose assemblies is performed, when required, by properly trained and permitted employees using suitable testing equipment and facilities.

Recharging required for completion of hydrostatic testing shall be included in the hydrostatic testing bid price and shall not be billed separately as “Recharge”.

Hydrostatic testing shall be performed when there is evidence of corrosion, mechanical damage or other reasons to question the integrity of the extinguisher or when extinguishers are due to be tested to meet the five (5) or twelve (12) year hydrostatic testing requirements of NFPA 10.

Hydrostatic testing shall be performed only by D.O.T. approved cylinder re-qualification facilities. Upon request by the City, bidding firms approved as cylinder re-qualification facilities must submit proof of D.O.T. approval.

Bidding firms that subcontract hydrostatic testing shall provide the company name, address and telephone number of the D.O.T. approved cylinder re-qualification facility to be used. The Convention Center’s contract will be with the successful bidder only. Any/all work performed by a subcontractor or payment to a subcontractor will be the sole responsibility of the successful bidder.

Extinguishers shall be visually examined both internally and externally prior to hydrostatic testing.

Upon completion of the hydrostatic testing, a verification of service collar indicating the month and year the service was performed shall be affixed to the extinguisher and all required information shall be recorded in accordance with applicable NFPA standards on a durable hydrostatic testing label and the label shall be securely affixed to the extinguisher. Metal stamping is not acceptable except that the hydrostatic test date shall be stamped into CO2 cylinders.

SCOPE OF WORK – EXHAUST HOOD CLEANING & INSPECTIONS

REQUIRED WORK

These specifications shall establish the minimum acceptable standards for servicing and maintaining of the hood cleaning Systems. The successful Contractor will be required to inspect, test and clean each system at the frequency specified for that system. The Contractor will also be responsible for performing routine/emergency repair service on an “as needed” basis for all specified equipment.

The successful Contractor shall be responsible for providing all parts, materials, supplies, tools, equipment, labor, supervision and transportation necessary to perform the specified services.

REQUIRED WORK

Upon award of the contract, the Contractor shall contact Convention Center listed in these specifications to determine when inspections, testing and cleanings are due for the hood cleaning system(s) located at the Convention Center. The Contractor shall be responsible for scheduling and performing, when due, the inspections, testing and cleaning of each system.

The Contractor shall service and maintain all hood cleaning systems in accordance with the manufacturer’s recommended procedures, these bid specifications and the terms and conditions stated herein.

Should any system require twelve (12) year maintenance during the term of this contract, it shall be the responsibility of the Contractor to schedule and perform the twelve (12) year maintenance service when due.

The Contractor shall also perform routine and emergency repairs on an “as needed” basis.

INSPECTIONS AND TESTING

All hood cleaning systems specified require two (2) inspections and testing per year.

Inspections and testing shall include, but is not limited to, the following (as applicable):

1.   Check for and identify any changes in the hazard area that may affect the performance and/or reliability of the system.

2.   Check date of manufacture to determine if twelve (12) year maintenance service is required or was performed when required.

3.   Examine both suppression agent and actuation cylinder shells and components for damage, corrosion, repairs or other physical conditions that might impair their functioning properly. Examine valve assemblies to ensure they are operating properly. Ensure pressure gauges are operating properly and match recommended operating pressures. Check cylinders to ensure that they are filled and charged to capacity and recharge if needed.

4.   Inspect and test all actuation components, including remote manual pull stations, mechanical/electrical devices, detectors and actuators for proper operation.

5.   Check gas/electrical shutoff functions to ensure they are operating properly.

6.   Check system components for cleanliness.

7.   Check all nozzles to ensure that they are properly aimed, free of blockage and proper

blow-off caps are intact.

8.   Inspect fusible links/automatic sprinkler heads/other types of detection devices and

clean/replace when needed in accordance with manufacturer recommendations.

9.   Inspect piping and conduit to ensure it was installed according to manufacturer’s specifications, is      not obstructed and is securely bracketed.

10.   Ensure tamper seals are intact.

11.   Ensure proper type of portable fire extinguisher is available, is easily accessible and has

been properly serviced.

12.   Record all required information on a durable service tag and securely affix tag to system.

Upon completion of each inspection and testing, a written inspection report shall be completed and shall contain a detailed description of the actual work performed. The report shall also fully explain any deficiencies noted and recommended actions to be taken in accordance with recognized procedures for care and maintenance. The report shall clearly identify the deficient system and the location of the system. An authorized City representative shall sign the inspection report and a copy of the report shall be provided to the City representative.

The Contractor shall also mail a copy of the inspection report to:

City of Myrtle Beach Fire Marshall

PO Box 2468

Myrtle Beach, SC 29588.

CLEANING

All hood cleaning systems shall be cleaned once a year. Cleaning of each system shall include the exterior of the system, hoods, backsplashes, grease removal devices, filters, fans, interior of all exhaust system ductwork, interior of all exhaust removal fans/blowers and all other appurtenances. All parts shall be cleaned to bare metal to completely remove all solidified, semi solidified or liquid cooking by-products. No flammable solvents or other flammable cleaning aids shall be used in the cleaning process. Cleaning chemicals shall not be applied on fusible links, other detection devices or the automatic extinguishing system. Parts shall not be coated with powder or other substance upon completion of cleaning and hoods shall be polished upon completion of cleaning.

Upon completion of the cleaning process, exhaust fans/blowers shall be restarted, all access panels/doors and cover plates utilized during the cleaning process shall be replaced and fastened, dampers and diffusers shall be positioned for proper exhaust air flow and all electrical switches and system components shall be returned to an operable state.

Upon completion of the system cleaning, the immediate work area shall be properly cleaned, any debris resulting from the cleaning process shall be removed and properly disposed of and the kitchen/concession areas shall be left ready for use by the staff.

Upon completion of cleaning, a certificate indicating date of cleaning, name of servicing company and name of individual performing the work shall be completed along with a written report identifying any inaccessible area(s) or any other area(s) that was/were not cleaned. Both the certificate and written report shall be provided to the City facility point of contact person.

Time charged for all repairs shall begin upon arrival and beginning of work at the job site and shall end upon completion of work and departure from the job site.

Work required that does not constitute an emergency, but should be completed as soon as possible to eliminate inconvenience to occupants shall be defined as a routine repair. Work required that poses an immediate safety hazard, reduces operational effectiveness, or may result in damage to the facility shall be defined as an emergency repair.

The Contractor shall contact the Convention Center requesting routine repair service within twenty-four (24) hours after receiving notification of the need for repair. Unless instructed otherwise by an authorized City representative, routine repairs shall be completed during normal business hours as soon as possible after notification of the need for repair services. Normal business hours shall be defined as 8:00 am – 5:00 pm, Monday – Friday, excluding City holidays.

The Contractor shall immediately contact a City facility requesting emergency repair service and unless otherwise instructed by City personnel, shall respond on-site within two (2) hours after receiving notification of the need for repair. The City shall bear the sole responsibility in determining what constitutes an emergency and the Contractor shall respond on-site upon the City’s request.

When emergency repairs are completed during normal business hours as previously defined, the repairs shall be billed at the routine repair service hourly labor rate, unless the two (2) hour on-site response time was required and met, in which case the emergency repair service hourly labor rate will apply.

Prior to performing a repair, the contractor shall provide the City with the estimated cost, to include both labor cost and cost for part(s), to complete the repair. After receiving authorization from the City, the contractor shall proceed with the work. The City shall not be responsible for the cost of any completed repair(s) that has/have not been approved in advance by the City.

The City may, at the City’s option, request a written quote for any needed repair prior to approving the repair. When requested, the written quote shall be provided no later than two (2) working days from date of request. The quote shall include: 1) full description of work to be performed, 2) total number of labor hours to complete the work, 3) itemized list of required parts and unit cost of each, 4) total cost to complete the work. It shall be the contractor’s responsibility to ensure that the contractor has all information necessary to prepare as accurate a quote as possible. Upon authorization to complete the work when a written quote has been provided, actual cost of the work and/or parts shall not exceed the quoted price without prior approval of an authorized City representative.

Upon completion of each repair, a written service report shall be completed and shall contain a detailed description of the actual work performed, an itemized list of any worn, damaged or defective parts replaced and total number of labor hours worked. An authorized City representative shall sign the service report and a copy of the report shall be provided to the City representative.

At any time the contractor consistently fails to respond to service calls within the allotted response time, the City may consider the contractor in default and the contract shall be subject to cancellation. Consistent failure is defined as not responding within the allotted response time at any or all facilities on two out of four consecutive occurrences.

ADDITIONAL TERMS AND CONDITIONS

- Include with your proposal at least two (2) references of similar work performed by your company. Telephone number and person to contact must be included for proposal consideration.

| a) | __________________________________________________________________ |
| --- | --- |
|  | __________________________________________________________________ |
|  | __________________________________________________________________ |
|  | __________________________________________________________________ |
| b) | __________________________________________________________________ |
|  | __________________________________________________________________ |
|  | __________________________________________________________________ |
|  | __________________________________________________________________ |

- Include with your proposal any written warranties that apply.

- Insurance Requirements are attached. Work cannot begin until a valid Certificate is provided meeting all requirements. A Performance and Payment Bond in the amount of 100% of the contract price will be required. The Certificate of Insurance and the Performance and Payment Bonds must be provided on the attached forms by the successful proposer after notification of intent to award.

- List any exceptions to specifications:

_______________________________________________________________________

_______________________________________________________________________

_______________________________________________________________________

_______________________________________________________________________

5.   A City Business License will be required prior to commencement of work. For information

contact the Business License Office at (843) 918-1200.

City of Myrtle Beach

INSURANCE REQUIREMENTS

PUBLIC LIABILITY AND PROPERTY DAMAGE

The Contractor shall purchase and thereafter maintain for the term of this agreement, and any subsequent extensions hereto, public liability insurance to protect Contractor from claims for bodily injury and/or property damage which may result from Contractor’s performance of this agreement. The policy shall provide a combined single limit of liability of $1,000,000 per occurrence for bodily injury and property damage with an aggregated limit of not less than $1,000,000.

AUTOMOBILE LIABILITY

The Contractor shall purchase and thereafter maintain for the term of this agreement and any subsequent extensions hereto, comprehensive automobile liability insurance to protect the Contractor from claims for bodily injury and property damage which may arise from Contractor’s use of motor vehicles in the performance of this agreement. The policy shall provide for a combined single limit of $1,000,000 per occurrence for bodily injury and property damage.

WORKERS’ COMPENSATION INSURANCE

Prior to beginning the work, the Contractor shall take out full compensation insurance for all persons which may be employed directly or indirectly in the performance of this agreement, coverage is to apply to all employees for statutory limits in compliance with the applicable state and federal laws. The policy must provide Employers Liability coverage in the amount of $500,000 each accident; $500,000 bodily injury by disease each employee and $500,000 bodily injury by disease policy limit and shall be maintained in full force and effect during the term and any subsequent extensions hereto.

EXCESS LIABILITY POLICY

At the option of the Contractor, the limits of the primary general liability, automobile liability and employer’s liability policies may be less than stipulated herein, with an excess policy providing the additional limits needed. This form of coverage must be approved by the City and will only be acceptable when both the primary and excess policies include the coverage and endorsements required herein.

POLICY ENDORSEMENTS

The following requirements shall apply to the policy(s) indicated below:

- General Liability and Automobile Liability

It is understood and agreed that the City of Myrtle Beach, its officials, agents and employees are recognized as additionally named insureds under the policy and, as such, will be provided thirty (30) days written notice by registered mail of non-renewal, exhaustion of aggregate limit, modification of coverage or cancellation for any reason, and the company hereby agrees to provide such notice. Failure of the company to provide the required notice shall cause the coverage to continue in force for the benefit of the City, its officials, agents and employees until proper notification, as required herein, is provided, the provisions of the policy or any Certificate of Insurance to the contrary notwithstanding.

- Workers’ Compensation

The cancellation provision is hereby amended to provide that the City of Myrtle Beach will be provided thirty (30) days written notice via certified mail, return receipt required, in the event of coverage cancellation.

NOTIFICATION OF INSURANCE COMPANIES

It is the responsibility of the Contractor to notify all insurance companies to familiarize themselves with all the terms and conditions of this agreement. The insurance companies shall waive their right of

### INSURANCE REQUIREMENTS continued

notification by the City of any change or modification of this contract, or of decreased or increased work, or of the cancellation of this agreement or of any other acts by the City or its authorized employees or agents under the terms of this agreement. The waiver by the insurance companies shall in no way relieve them of their obligations under this agreement.

CERTIFICATES OF INSURANCE

Contractor shall file with the City a Certificate of Insurance, which shall be approved by the City prior to the inception of any work. Renewal certificates shall be sent to the City thirty (30) days prior to any expiration date.

INSURER LICENSING AND RATING

All insurance companies providing coverage to the City, shall be licensed to do business in the State and have an A.M. Best rating of “A-“ or better.

INSURANCE COVERAGE ADJUSTMENTS

In response to changing circumstance of loss exposures, the City reserves the right to modify the insurance coverage, limits of liability, policy endorsements and policy terms required in this contract. The City will provide written notice to the Contractor, which outlines such changes and allow Contractor a reasonable period of time in which to comply with the new requirements. However, in no event shall Contractor compliance period be longer than thirty (30) days.

COVERAGE CANCELLATION OR UNSATISFACTORY COVERAGE

If at any time any of the foregoing policies shall be or become unsatisfactory to the City, as to form or substance, or if a company issuing any such policy shall be or become unsatisfactory to the City, the Contractor shall, upon notice to that effect from the City, promptly obtain a new policy and submit the same for approval to the City. Upon failure of the Contractor to furnish, deliver and maintain the insurance coverage’s required herein, this agreement, at the sole discretion of the City, may be forthwith declared suspended, discontinued or terminated. Failure of the Contractor to take out and/or maintain any required insurance shall not relieve the Contractor from any liability under this agreement, nor shall the insurance requirements be construed to conflict with or otherwise limit the obligations of the Contractor concerning indemnification.

HOLD HARMLESS

Contractor agrees to protect, defend, indemnify and hold the City, its officers, employees and agents free and harmless from and against any and all losses, penalties, damages, settlements, cost, charges, professional fees or other expenses and liabilities of every kind and character arising out of, or relating to, any and all claims, liens, demands, obligations, actions, proceedings or causes of action of every kind in connection with or arising out of this agreement, and/or the performance hereof, that are due to the negligence of the Contractor, its officers, employees or agents. The Contractor further agrees to investigate, handle, respond to, provide defense for and defend the same at its sole expense and agrees to bear all other costs and expenses related thereto.

## INSURANCE REQUIREMENTS continued

### SAMPLE

| #### CERTIFICATE OF INSURANCE |  |  |  |  |  |  |  | CERTIFICATE NUMBER |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ##### PRODUCER Insurance Agent Name 4000 Insurance Pkwy Anytown, USA 99999 |  |  | THIS CERTIFICATE IS ISSUED AS A MATTER OF INFORMATION ONLY AND CONFERS NO RIGHTS UPON THE CERTIFICATE HOLDER OTHER THAN THOSE PROVIDED IN THE POLICY. THIS CERTIFICATE DOES NOT AMEND, EXTEND OR ALTER THE COVERAGE AFFORDED BY THE POLICIES DESCRIBED HEREIN. |  |  |  |  |  |  |
|  |  |  |  |  | ##### COMPANIES AFFORDING COVERAGE |  |  |  |  |
| ##### INSURED Bidding Firm’s Name 1000 Any Street Anytown, USA 99999 |  |  | ###### COMPANY A ABC INSURANCE COMPANY COMPANY B COMPANY C COMPANY D |  |  |  |  |  |  |
| COVERAGES-THIS CERTIFICATE SUPERCEDES AND REPLACES ANY PREVIOUSLY ISSUED CERTIFICATE FOR THE POLICY NOTED BELOW |  |  |  |  |  |  |  |  |  |
| This is to certify that policies of insurance described herein have been issued to the insured named herein for the policy indicated. Notwithstanding any requirement, term or condition of any contract or other document with respect to which the certificate may be issued or may pertain, the insurance afforded by the policies described herein is subject to all the terms, conditions and exclusions of such policies. Aggregate limits shown may have been reduced by paid claims. |  |  |  |  |  |  |  |  |  |
| CO LTR | TYPE OF INSURANCE | POLICY NUMBER |  | POLICY EFFECTIVE DATE (MM/DD/YY) |  | POLICY EXPIRATION DATE (MM/DD/YY) | LIMITS |  |  |
| A | General Liability X Commercial General Liability _ Claims Made X Occur _ Owners & Contractor’s Prot ________________ | XYZ1234 |  | 00/00/00 |  | 00/00/00 | General Aggregate Products-Comp/Op Agg Personal & Adv Injury Each Occurrence Fire Damage (any 1 fire) |  | $ 1,000,000 $ 1,000,000 $ 1,000,000 $ 1,000,000 $ 50,000 |
| A | Automobile Liability X Any Auto _ All Owned Autos _ Scheduled Autos X Hired Autos X Non-Owned Autos ________________ | XYZ1234 |  | 00/00/00 |  | 00/00/00 | Combined Single Limit Bodily Injury (Per person) Bodily Injury (Per accident) Property Damage |  | $ 1,000,000 $ $ $ |
|  | Garage Liability _ Any Auto ________________ |  |  | 00/00/00 |  | 00/00/00 | Auto Only-Ea Accident Other than auto only: Each Accident Aggregate |  | $ $ $ |
|  | Excess Liability _ Umbrella Form _ Other than Umbrella Form |  |  | 00/00/00 |  | 00/00/00 | Each Occurrence Aggregate |  | $ $ |
| A | Workers Compensation (and Employer’s Liability) The Proprietor/Partners Executive Officers Are: X Inc _ Excl | XYZ1234 |  | 00/00/00 |  | 00/00/00 | X WC Statutory Limits _ Other EL Each Accident EL Disease-Policy Ltd EL Disease-Ea Employee |  | $ 500,000 $ 500,000 $ 500,000 |
|  | Other |  |  |  |  |  |  |  |  |
| Description of Operations/Locations/Vehicles/Special Items: City of Myrtle Beach is named as additional insured with respect to General and Automobile Liability |  |  |  |  |  |  |  |  |  |
| CERTIFICATE HOLDER |  |  |  | CANCELLATION |  |  |  |  |  |
| City of Myrtle Beach Attn: Purchasing Division Drawer 2468 Myrtle Beach, SC 29578-2468 |  |  |  | Should any of the policies described herein be cancelled before the expiration date thereof, the insurer affording coverage will endeavor to mail 30 days written notice to the certificate holder named herein, but failure to mail such notice shall impose no obligation or liability of any kind upon the insurer affording coverage, its agents or representatives, or the issuer of this certificate. |  |  |  |  |  |
|  |  |  |  | ##### INSURANCE AGENT SIGNATURE |  |  |  |  |  |

Price Schedule

Fire Alarm System, Sprinkler Maintenance

Fire Extinguisher and Exhaust Hood Cleaning Maintenance

PROJECT NO.: 18-R0030

| Mandatory Pre-Proposal Conference: Attendance is required for proposal consideration | Tuesday, May 15, 2018 @ 10:00 Myrtle Beach Convention Center 2101 N Oak Street Myrtle, Beach, SC Meet in front lobby next to escalator |
| --- | --- |
| Opening Date & Time: | Tuesday, May 22, 2018 at 2:00PM |

Fire Alarm System & Sprinkler/pump system

| CONVENTION CENTER Inspection and Testing Fire Alarm and Detection System Fire Sprinkler System Fire Pump System Class III Standpipe System | $___________/Semi-annual $___________/Semi-annual $___________/Semi-annual $___________/Annual |
| --- | --- |

ROUTINE/EMERGENCY REPAIR SERVICE HOURLY LABOR RATE FOR CONVENTION CENTER

Please indicate below hourly labor rate for repair service.

All costs, including but not limited to, truck charges, travel time, per diem, mileage and fuel shall be included in repair service hourly labor rate bid prices. The cost for parts, if required, will be the only charge allowed to be billed separately.

| FIRE ALARM AND DETECTIONS SYSTEMS |  |
| --- | --- |
| 37. Routine Repair Service Labor Rate: 38. Emergency Repair Service Labor Rate: | $__________/hr $__________/hr |
| FIRE SPRINKLER SYSTEMS |  |
| 39. Routine Repair Service Labor Rate: 40. Emergency Repair Service Labor Rate: | $__________/hr $__________/hr |
| FIRE PUMP SYSTEMS |  |
| 41. Routine Repair Service Labor Rate: 42. Emergency Repair Service Labor Rate: | $__________/hr $__________/hr |

Company Name: _____________________________________

Authorized Signature:_________________________________

Email Address:_______________________________________

Price Schedule

Fire Extinguisher

|  | ## Description/Size | ## Qty | Annual Maintenance |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Multi-Purpose Dry Chemical – ABC 20 lb. | 1 ea | $___________ |  |  |  |  |  |
|  | Recharge $_______/ea Hydrostatic Testing $_______/ea Six (6) Year Maintenance Service $_______/ea |  |  |  |  |  |  |  |
|  | Multi-Purpose Dry Chemical - ABC 10 lb. | 1 ea | $___________ |  |  |  |  |  |
|  | Recharge $_______/ea Hydrostatic Testing $_______/ea Six (6) Year Maintenance Service $_______/ea |  |  |  |  |  |  |  |
|  | Multi-Purpose Dry Chemical - ABC 6 lb. | 1 ea | $___________ |  |  |  |  |  |
|  | Recharge $_______/ea Hydrostatic Testing $_______/ea Six (6) Year Maintenance Service $_______/ea |  |  |  |  |  |  |  |
|  | Multi-Purpose Dry Chemical - ABC 5 lb. | 1 ea | $___________ |  |  |  |  |  |
|  | Recharge $_______/ea Hydrostatic Testing $_______/ea Six (6) Year Maintenance Service $_______/ea |  |  |  |  |  |  |  |

K-Class					     1 ea         $___________

Recharge     $_______/ea

Hydrostatic Testing     $_______/ea

Six (6) Year Maintenance Service     $_______/ea

|  | Multi-Purpose Dry Chemical - ABC 2.5 lb | 1 ea | $___________ |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Recharge $_______/ea Hydrostatic Testing $_______/ea Six (6) Year Maintenance Service $_______/ea |  |  |  |  |  |

Company Name: _____________________________________

Authorized Signature:_________________________________

Email Address:_______________________________________

Price Schedule

Exhaust Hood Cleaning & Inspection

Inspection and Testing of Exhaust Hood

| Description | Unit | Price Per Inspection | Extended Price (Annually) |
| --- | --- | --- | --- |

Convention Center	Twice Yearly		$_________			$___________

Convention Center	Annually		$_________			$___________

Cleaning of Exhaust Hood

Convention Center	Annually		$_________			$___________

Maintenance on Exhaust Hood

Convention Center	as need per call	$_________			$___________

Repair Service								Hourly Labor Rate

Routine Repair Service						$____________/hr

Emergency Repair Service						$____________/hr

Please indicate percentage over cost to be charged for parts:		$_____________

2nd Year: _____%  (to be applied to original bid prices)

3rd Year: _____%  (to be applied to second year prices)

4th Year: _____%  (to be applied to third year prices)

5th Year: _____%  (to be applied to fourth year prices)

AUTHORIZED SIGNATURE: __________________________________________________

COMPANY NAME: ___________________________________________________________

EMAIL ADDRESS:____________________________________________________________

Bid prices shall be DELIVERED PRICES (FOB Destination) and are to include all shipping costs, including but not limited to, loading/unloading cost(s), fuel charge(s), sales tax, fuel surcharge(s) energy surcharge(s) and environmental fee(s). The City will not be responsible for any demurrage charge(s).

BID AWARD

Award will be made in whole to one (1) contractor. Award will be made in the best interest of the City.

INVOICING

Invoicing shall be submitted upon completion of shipment.  All invoices must reference the purchase order number, quantity, unit price and extended price of item purchased.

| Invoices shall be submitted to: | City of Myrtle Beach/Convention Center 2101 North Oak Street Myrtle Beach, SC 29577 |
| --- | --- |

PROPOSAL AND SIGNATURE DOCUMENT

# Bid Number:  18-R0030

The undersigned, as proposal, declare that we have examined all bid documents contained herein and will contract, thereon, with the City of Myrtle Beach (hereinafter referred to as the "City") to do everything necessary for the fulfillment of this contract. We agree any addenda received are part of the proposal documents. (If no addenda has been received, please place a zero in the space provided.)

In addition, we propose to furnish the following products/services in strict conformance to the proposal specifications and proposal invitation issued by the City of Myrtle Beach for this proposal. Any exceptions are clearly noted as required.

We understand that any false statements made to meet any requirements may result in contract cancellation or initiation of action under Federal or State laws or both.

| _________________________________ Bidder-Company Name |  |  | _________________________________ Addenda Numbers Received |
| --- | --- | --- | --- |
| _________________________________ City Business License Number |  |  | _________________________________ Telephone Number |
| _________________________________ Authorized Signature |  |  | _________________________________ Fax Number |
| _________________________________ Printed Name |  |  | _________________________________ Email |
| South Carolina Sales Tax Registration No.: ___________________________________________ |  |  |  |
| If SC Sales Tax No. not supplied, please state reason: ___________________________________ |  |  |  |
| Federal Tax ID No. (FEIN): _______________________________________________________ |  |  |  |
| _________________________________ Mailing Address |  |  | ____________________ Date |
| _________________________________ City, State, Zip |  |  |
| _________________________________ Remittance Address (If different from mailing address) __________________ |  |  |  |  |
| ________________________________ City, State, Zip |  |  |  |  |

|  | CITY OF MYRTLE BEACH LOCAL VENDOR PREFERENCE TO QUALIFY FOR LOCAL PREFERENCE FORM MUST BE SUBMITTED WITH BID |
| --- | --- |
| First in Service |  |

APPLICATION OF ELIGIBILITY TO QUALIFY FOR LOCAL VENDOR PREFERENCE WITHIN THE DEFINED BOUNDARIES: MYRTLE BEACH CITY LIMITS, HORRY COUNTY, NESA AREA (NESA area is comprised of Horry, Georgetown, Williamsburg, Florence, Marion, Darlington, Dillon, Chesterfield, and Marlboro Counties).

| City of Myrtle Beach Business License: (To qualify for Local Vendor Preference vendor must have a current City of Myrtle Beach Business License a minimum of ninety (90) days prior to the request for bid/ proposal being made public) |  |  |
| --- | --- | --- |
| City of MB Business License Number: ______________ *NOT Horry County License Number | Date issued: ______________ |

Complete all areas below. Incomplete forms may be rejected.

| 1. | LEGAL NAME OF BUSINESS: |  |  | __________________________________________ |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Mailing Address: |  |  |  |  | ________________________________________ ________________________________________ |  |  |  |  |
|  | Physical Address: (To qualify vendor must have maintained a physical address and office as a principal place of business within the defined boundaries of the category sought for at least one (1) year, and during that time have had a majority of full-time employees, chief officers and managers regularly conducting work and business from this office.) |  |  |  |  | ________________________________________ ________________________________________ |  |  |  |  |
| 2. | Year business was established in the City of Myrtle Beach / Horry County / NESA area: |  |  |  |  |  |  |  |  |  |
|  | Year: | ______________ |  |  |  |  | County: | ______________ |  |  |
|  |  |  |  |  | (Name of County) |  |  |  |  |  |
| ************************************************************************************ |  |  |  |  |  |  |  |  |  |  |  |
| Under penalty of perjury, the undersigned states that the foregoing statements are true and correct. The undersigned also acknowledges that any person, firm, corporation or entity intentionally submitting false information to the City in an attempt to qualify for local preference shall be prohibited from bidding on City of Myrtle Beach products and services for a period of one (1) year. |  |  |  |  |  |  |  |  |  |  |
| Authorized Signature: |  |  | ____________________________________ |  |  |  |  |  | Date: | ______________ |
| Printed Name & Title: |  |  | ____________________________________ |  |  |  |  |  | Phone: | ______________ |

LOCAL VENDOR PREFERENCE continued

| Bid Amount | Within City Limits | Within Horry County | Within NESA Area |
| --- | --- | --- | --- |
| Up to $5000.00 | 5% of Bid | 4% of Bid | 3% of Bid |
| $5001.00 to $10,000.00 | $250.00 plus 4% of amount between $5001.00 and $10,000.00 | $200.00 plus 3% of amount between $5001.00 and $10,000.00 | $150.00 plus 2% of amount between $5001.00 and $10,000.00 |
| $10,001.00 and up | $450.00 plus 3% of amount above $10,000.00 with the maxium being $2000.00, including the $450.00 | $400.00 plus 2% of amount above $10,000.00 with the maxium being $1800.00, including the $400.00 | $300.00 plus 1% of amount above $10,000.00 with the maxium being $1600.00, including the $300.00 |

If company/individual performs services on City property a Certificate of Insurance must be provided prior to commencement of work meeting requirements of the City.

The vendor must submit a copy of their Local Vendor Preference Certificate with their bid.

An eligible business shall maintain such status throughout the term of any contract with the City. Failure to maintain such status or to keep current on all fees and taxes owed the City shall be grounds to terminate the contract.

LIST OF SUBCONTRACTORS   Attachment 002

The undersigned stated that the following is a full and complete list of the proposed subcontractors on this Project and the class of work to be performed by each, and that such list will not be added to nor altered without written consent of the Owner.

|  | Subcontractor and Address | Class of Work to be Performed |
| --- | --- | --- |
| 1) | ___________________________________ | _______________________ |
|  | ___________________________________ | _______________________ |
| 2) | ___________________________________ | _______________________ |
|  | ___________________________________ | _______________________ |
| 3) | ___________________________________ | _______________________ |
|  | ___________________________________ | _______________________ |
| 4) | ___________________________________ | _______________________ |
|  | ___________________________________ | _______________________ |
| 5) | ___________________________________ | _______________________ |
|  | ___________________________________ | _______________________ |
| 6) | ___________________________________ | _______________________ |
|  | ___________________________________ | _______________________ |
| 7) | ___________________________________ | _______________________ |
|  | ___________________________________ | _______________________ |

Dated:________________________________	Bidder:___________________________

Signed: ___________________________

Title: _____________________________

Phone #:___________________________