UPS System Maintenance & PM Requirements

- One (1) year full maintenance coverage: (2 Liebert UPS & 5 STS)

- Emergency Service 7x24, 365

- All parts, labor and expenses

- Response time: four (4) hours or less

- One PM Inspections: (2 Liebert UPS @ 5 STS)

- System overview with customer and detailed inspection report

Vendor must be an authorized service provider for Liebert power product lines (uninterruptible power supply/battery, static transfer switch, etc.) Documentation showing authorized service provider status must be  submitted with quote.

STATIC TRANSFER SWITCH

SCOPE OF WORK

- Perform a complete visual inspection of the equipment, including sub-assemblies, wiring harnesses, contacts, cables and major components.

- Check all mechanical connections for tightness and heat discoloration, making corrections where necessary.

- Clean foreign material and dust from internal compartments. Perform a status check of alarm circuits.

- Calibration of the equipment to meet manufacturer’s specifications.

- Operational checkout of the system to include transfers and proper status indications.

- Install or perform Engineering Field Change Notices (FCN) as necessary.

- Return unit to operational service with normal load then measure and verify display indications.

- Perform additional checks as consistent with customary commercial practice.

- Review system performance with customer to address any questions and to schedule any repairs.

- Provide a detailed written report noting any deficiencies and corrective action needed, taken and/or planned.

BATTERY SYSTEM

SCOPE OF WORK

- Clean normal cell top dirt accumulation.

- Measure and record the total battery float voltage and charging current.

- Measure and record the overall AC ripple voltage.

- Visually inspect the jars and covers for cracks and leakage.

- Visually inspect for evidence of corrosion.

- Measure and record the ambient temperature.

- Verify the integrity of the battery rack/cabinet.

- Measure and record 100% of the jar temperatures.

- Measure and record the float voltage of all jars.

- Measure and record all internal ohmic readings.

- Re-tighten all connections to the battery manufacturer's specifications, if required.

- Measure and record all battery connection resistances in micro-ohms, when applicable.

- Refurbish cell connections as deemed necessary.

- Check integrity of battery cabinet.

- Check for NO-OX grease or oil on all connections (if applicable).

- Check battery jars for proper liquid level (if flooded cells).

- Check for corrosion on all the terminals and cables.

- Examine the physical cleanliness of the battery room and jars.

- Measure and record DC bus ripple voltage (if applicable). Measure and record total battery float voltage.

- Perform additional checks as consistent with customary commercial practice.

- Review system performance with customer to address any questions and to schedule any repairs.

- Provide a detailed written report noting any deficiencies and corrective action needed, taken and/or planned.

UNINTERRUPTIBLE POWER SYSTEMS

SCOPE OF WORK

- Perform temperature check on all breakers, connections, and associated controls. Repair and/or report all high temperature areas.

- Perform a complete visual inspection of the equipment including subassemblies, wiring harnesses, contacts, cables, and major components.

- Check air filters for cleanliness. (if applicable)

- Check rectifier and inverter snubber boards for discoloration.

- Check power capacitors for swelling or leaking oil.

- Check for DC capacitor vent caps that have extruded more than 1/8". (if applicable)

- Record all voltage and current meter readings on the module control cabinet or the system control cabinet.

- Measure and record harmonic trap filter currents.

- Check the inverter and rectifier snubbers.

- Check all nuts, bolts, screws, and connectors for tightness and heat discoloration.

- Check fuses on the DC capacitor deck for continuity (if applicable).

- With customer approval, perform operational test of the system including unit transfer and battery discharge.

- Calibrate and record all electronics to system specifications.

- Check or perform Engineering Field Change Notices (FCN) as necessary. Measure and record all low-voltage power supply levels.

- Record phase-to-phase input voltage and currents.

- Perform additional checks as consistent with customary commercial practice.

- Review system performance with customer to address any questions and to schedule any repairs.

- Provide a detailed written report noting any deficiencies and corrective action needed, taken and/or planned.

UPS SYSTEM INFO

- Liebert s610 SMS UPS		Model # UDA63154A36AD68 	Tag # 1303573

Battery:

Manufacturer: ENERSYS				No of Jars: 40

Model: HX505-FR					Cells per Jar: 6

Battery Type: VRLA					Cells per string: 240

MBCPM 	Model# U36MB15430AA25S  		TAG# 1303576

- Liebert s610 SMS UPS		Model # UDA63154A36AD68 	Tag # 1303573

Battery:

Manufacturer: ENERSYS				No of Jars: 40

Model: HX505-FR					Cells per Jar: 6

Battery Type: VRLA					Cells per string: 240