Escambia County Public Safety, Communications Division is soliciting quotes for:

Equipment or Service:

A qualified contractor to relocate all established microwave radio and associated equipment and transmission lines from existing radio shelter to a replacement radio shelter and remove and dispose of old equipment.

Location:

North Site		7955 Bratt Rd.

Tower Information:	FCC# 1028867

Selected Vendor Requirements:

- Relocate (5-6) equipment racks and associated equipment and 17 transmission lines

- Coordinate with each agency to determine channel downtime and alternate plan

- Coordinate with and relocate Department of Forestry repeater

- Coordinate with and dispose of unused City of Pensacola equipment

- Remove and dispose of unused racks in new shelter (7-10)

- Relocate dehydrator & lines

- Relocate Digital Paging repeater

- Relocate Flash tower lighting equipment

- Relocate surge suppression unit(s)

- Relocate TRAC units

- Relocate UPS

- Seal transmission line entry points

- Ground equipment according to manufactures recommendation or Motorola R56 standards and guidelines

- Vendor must regularly perform land mobile radio (LMR) work as the main focus of their company business.

- Vendor to coordinate with and procure any service needed from Motorola Solutions for engineering or modification work needed to maintain the system in its current state.

- Vendor must establish and integrate current alarms into the existing Motorola Moscad alarm reporting system including: door, smoke, high temp, low temp, tower lights, surge arrestor, UPS, generator run, and microwave alarms.

- Vendor must supply three references for projects similar in size and scope with the proposal.

- Vendor’s tower workers must possess a valid Comtrain or equivalent Basic Tower Safety and Rescue training certification and must provide proof of such training certification with the proposal.

- Vendor must provide the full manufacture warranty on materials purchased and three (3) year warranty on workmanship from the final date of acceptance.

- System shall be tested to demonstrate satisfactory functional and operating efficiency.

- All work shall be completed according to the manufacturer’s instructions, specifications, and/or standard trade practices.

- Identified equipment shall be removed and disposed of at the vendors expense.

- All electrical work shall be included in quote

Any requirement placed on the County for the project must be specifically identified in the respondent’s quote. Any requirement for project completion that has not been identified and agreed upon as a County responsibility will be the responsibility of the vendor at no additional cost to the County.

This shall be a complete, turnkey, relocation project. It shall be understood and agreed upon that the quote includes each component for material and labor, even though every item involved is not listed herein. The vendor shall be responsible to provide ALL labor and materials (including electrical and grounding) for the entire scope of the project.

Vendor shall schedule a site visit prior to bid to ensure entire scope of work is fully understood.  Vendor is responsible to verify information needed to provide a complete and accurate quote.

Contact: Communications Chief, Andrew Hamilton (850.471.6316).