601 Hwy 297A Cantonment Florida 32514 (Escambia County Road Department Garage)

Replace the two Automatic Transfer Switches with a Single Transfer Switch

Project Intent:

Escambia County is seeking proposals to replace the two existing Auto transfer Switch with one Auto Transfer switch and change any service equipment necessary to meet code. A full 1-year Material and Labor Warranty shall be included with all proposals. A non-mandatory site visit will be available on February 26, 2020 at 10 am. It is the responsibility of the proposing Contractors to advise the County of any items, during the walk-through, that they feel are not adequately addressed in the Scope of Work for the adequate replacement of the existing Auto Transfer Switch(s). The Scope of Work will be revised, if required, and then sent to all Contractors so the items can be included in their bid.

General Notes:

Scope of Work:                                                                                                                                                        The intent of this project is to replace the two auto transfer switches that are fed from a single panel and fed by a generator only.  A single 600amp 480/277 vac main panel feeds the two transfer switches; separate panels are fed from each transfer switch for building power. This building is a truck and equipment garage with limited work being done on Friday and Monday.

Requirements:                                                                                                                                                      The Auto Transfer Switch must be compatible with a Onan 200KW 200.OD45 DYG  Generator                                                                                                                                                                                                                                                                                This work will be done during normal business hours.                                                                                                                                                                                                                                                                                                                       The Contractor is responsible for obtaining and paying for all applicable permits and fees.                                  The Contractor is responsible to maintain the work site in a safe and presentable condition.                               The Contractor will remove and dispose of all construction debris at the end of each work day.

Please call with any questions or email at jadanley@myescambia.com.

Allen Danley

Electrical Supervisor

Escambia County

Facilities Management Department

Phone:850 595-4635